Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 105.57 | P11:25:EES:WATERF:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 105.57 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 105.57 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 105.85 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 105.85 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 105.94 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 107.15 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 109.59 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07159 | 104.78 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07159 | 104.78 | 659425 SD.LS-KS-MB3 345 763666 G21-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07159 | 104.78 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07162 | 104.82 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07162 | 104.82 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07162 | 104.85 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07166 | 104.35 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07167 | 104.36 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07173 | 104.88 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07184 | 105.27 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07184 | 105.27 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07198 | 105.9 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07198 | 105.92 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07201 | 105.46 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07202 | 105.65 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07202 | 105.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07203 | 105.08 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07204 | 105.74 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0722 | 105.78 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0722 | 105.79 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0722 | 105.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07331 | 106.98 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07335 | 107.25 | 526936 YOAKUM 7 345 764866 G20-059-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07478 | 108.77 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07478 | 108.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07548 | 106.19 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0758 | 110.98 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07938 | 114.64 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08085 | 123.69 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08085 | 123.94 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 117.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 120.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 122.95 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 123.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 123.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08119 | 119.08 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08119 | 119.96 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08358 | 118.23 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08379 | 118.5 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08379 | 118.5 | Potential P4 Event - POI 515800_18 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08379 | 118.56 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0918 | 134.76 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0918 | 134.76 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 3 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997570 SIEM 8743066 230 4 | 675 | 675 | 0.08348 | 101.53 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997571 SIEM 8743066 230 3 | 675 | 675 | 0.08348 | 101.53 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 SIEM 8743066 230 2 | 559 | 643 | 0.08 | 102.1 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 SIEM 8743066 230 2 | 559 | 643 | 0.08348 | 106.59 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1385 | 1385 | 0.15387 | 102.96 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1385 | 1385 | 0.15387 | 102.85 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06828 | 112.31 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07013 | 111.32 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07147 | 103.58 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07155 | 103.58 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07156 | 103.89 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.62 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.63 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.81 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.88 | P13:138:EES:LC:T2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.92 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.92 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.93 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.94 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.94 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.96 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.97 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 103.97 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.01 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.49 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.5 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.52 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.52 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.52 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.53 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.56 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.57 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.57 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.59 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.68 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.72 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.72 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.75 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.75 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.77 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.77 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 104.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 105.04 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 105.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 105.21 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 106.59 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07157 | 109.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07162 | 103.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07162 | 103.84 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07162 | 103.86 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07166 | 103.41 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07167 | 103.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07173 | 103.89 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07184 | 104.52 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07184 | 104.52 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07198 | 105.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07198 | 105.11 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07201 | 104.68 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07202 | 104.87 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07202 | 104.87 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07203 | 104.07 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07204 | 104.95 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0722 | 104.98 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0722 | 105.02 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0722 | 105.02 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07331 | 106.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07335 | 106.48 | 526936 YOAKUM 7 345 764866 G20-059-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07478 | 107.99 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07478 | 108 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07548 | 105.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0758 | 110.38 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07938 | 114.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08085 | 123.69 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08085 | 124.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 117.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 120.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 122.86 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 123.52 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 123.52 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08119 | 119.12 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08119 | 120.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08358 | 118.07 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08379 | 118.39 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08379 | 118.39 | POI 515800_23 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08379 | 118.42 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0918 | 133.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0918 | 133.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997570 SIEM 8743066 230 4 | 675 | 675 | 0.08348 | 100.57 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997571 SIEM 8743066 230 3 | 675 | 675 | 0.08348 | 100.57 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 SIEM 8743066 230 2 | 559 | 643 | 0.08 | 101.16 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 3 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 SIEM 8743066 230 2 | 559 | 643 | 0.08348 | 105.57 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | 2768 | 2768 | 0.25566 | 101.98 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | 2768 | 2768 | 0.25566 | 101.98 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08093 | 100.5 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08093 | 100.54 | Potential P4 Event - POI 511568_2 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08093 | 100.54 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08093 | 100.61 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08093 | 100.65 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08241 | 104.83 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08241 | 104.83 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08241 | 104.83 | Potential P4 Event - POI 511468_11 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08396 | 103.48 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08396 | 103.48 | Potential P4 Event - POI 588839_3 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.0968 | 125.64 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09839 | 126.36 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09839 | 126.75 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09839 | 126.75 | POI 515800_22 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09839 | 126.75 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09839 | 126.75 | Potential P4 Event - POI 560078_4 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09857 | 127.3 | Potential P4 Event - POI 515800_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.0968 | 131.15 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.09839 | 131.84 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.09839 | 132.38 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.09839 | 132.38 | POI 515800_22 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.09839 | 132.38 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.09839 | 132.38 | Potential P4 Event - POI 560078_4 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.09857 | 133.03 | Potential P4 Event - POI 515800_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.0968 | 125.49 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09839 | 126.12 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09839 | 126.59 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09839 | 126.59 | Potential P4 Event - POI 515800_9 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09839 | 126.59 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09839 | 126.59 | Potential P4 Event - POI 560078_4 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.09857 | 127.17 | Potential P4 Event - POI 515800_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.1124 | 145.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.1124 | 145.69 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 396 | 441 | 0.11701 | 102.07 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 396 | 441 | 0.11701 | 102.15 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 515045 SEMINOL7 345 560101 SEMINOLE765 765 1 | 2768 | 2768 | 0.26637 | 101.94 | 515045 SEMINOL7 345 560101 SEMINOLE765 765 2 | Cumulative Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 515045 SEMINOL7 345 560101 SEMINOLE765 765 2 | 2768 | 2768 | 0.26637 | 101.94 | 515045 SEMINOL7 345 560101 SEMINOLE765 765 1 | Cumulative Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.09468 | 127.36 | P42:345:OKGE:SB_GRNT7313:::: | Cumulative Impact | Gracemont to Minco 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.09468 | 127.36 | Potential P4 Event - POI 515800_1 | Cumulative Impact | Gracemont to Minco 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.09468 | 130.92 | P42:345:OKGE:SB_GRNT7313:::: | Cumulative Impact | Gracemont to Minco 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.09468 | 130.92 | Potential P4 Event - POI 515800_1 | Cumulative Impact | Gracemont to Minco 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.16589 | 104.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.16589 | 104.3 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.16589 | 104.3 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 385 | 385 | 0.11701 | 116.17 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 385 | 385 | 0.11701 | 116.26 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 840 | 840 | 0.07003 | 104.14 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 2 | Cumulative Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 2 | 840 | 840 | 0.07003 | 104.14 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07426 | 112.74 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07643 | 111.69 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07676 | 104.58 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0768 | 104.53 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07682 | 104.87 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.57 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.57 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.58 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.58 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.58 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.79 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.85 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.85 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.88 | P13:138:EES:LC:T2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.93 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.94 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.94 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.96 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.97 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.97 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.01 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.24 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.25 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.27 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.27 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.28 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.28 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.28 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.33 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.33 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.35 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.35 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.44 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.51 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.51 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.53 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.53 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.55 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.55 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.57 | P11:25:EES:WATERF:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.57 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.57 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.85 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.85 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.94 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 107.15 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 109.59 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07685 | 104.78 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07685 | 104.78 | 659425 SD.LS-KS-MB3 345 763666 G21-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07685 | 104.78 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07687 | 104.85 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07688 | 104.82 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07688 | 104.82 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07692 | 104.35 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07692 | 104.36 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07699 | 104.88 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07709 | 105.27 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07709 | 105.27 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07722 | 105.9 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07722 | 105.92 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07726 | 105.46 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07726 | 105.65 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07726 | 105.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07728 | 105.74 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07729 | 105.08 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07745 | 105.78 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07745 | 105.79 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07745 | 105.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07845 | 107.25 | 526936 YOAKUM 7 345 764866 G20-059-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07854 | 106.98 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07996 | 108.77 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07996 | 108.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08052 | 106.19 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 110.98 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08432 | 114.64 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0858 | 123.69 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0858 | 123.94 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08594 | 117.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08594 | 120.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08594 | 122.95 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08594 | 123.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08594 | 123.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08641 | 119.08 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08641 | 119.96 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08851 | 118.23 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08873 | 118.5 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08873 | 118.5 | Potential P4 Event - POI 515800_18 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08873 | 118.56 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.09854 | 134.76 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.09854 | 134.76 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 3 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997570 SIEM 8743066 230 4 | 675 | 675 | 0.08961 | 101.53 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997571 SIEM 8743066 230 3 | 675 | 675 | 0.08961 | 101.53 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 SIEM 8743066 230 2 | 559 | 643 | 0.08587 | 102.1 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 SIEM 8743066 230 2 | 559 | 643 | 0.08961 | 106.59 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1385 | 1385 | 0.16255 | 102.96 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1385 | 1385 | 0.16255 | 102.85 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07426 | 112.31 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07643 | 111.32 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07672 | 103.58 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0768 | 103.58 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07682 | 103.89 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.62 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.63 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.81 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.88 | P13:138:EES:LC:T2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.92 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.92 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.93 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.94 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.94 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.96 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.97 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 103.97 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.01 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.49 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.5 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.52 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.52 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.52 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.53 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.56 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.57 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.57 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.59 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.68 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.72 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.72 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.75 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.75 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.77 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.77 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 104.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.04 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 105.21 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 106.59 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07683 | 109.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07687 | 103.86 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07688 | 103.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07688 | 103.84 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07692 | 103.41 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07692 | 103.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07699 | 103.89 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07709 | 104.52 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07709 | 104.52 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07722 | 105.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07722 | 105.11 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07726 | 104.68 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07726 | 104.87 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07726 | 104.87 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07728 | 104.95 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07729 | 104.07 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07745 | 104.98 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07745 | 105.02 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07745 | 105.02 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07845 | 106.48 | 526936 YOAKUM 7 345 764866 G20-059-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07854 | 106.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07996 | 107.99 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07996 | 108 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08052 | 105.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08098 | 110.38 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08432 | 114.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0858 | 123.69 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0858 | 124.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08594 | 117.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08594 | 120.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08594 | 122.86 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08594 | 123.52 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08594 | 123.52 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08641 | 119.12 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08641 | 120.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08851 | 118.07 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08873 | 118.39 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08873 | 118.39 | POI 515800_23 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08873 | 118.42 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.09854 | 133.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.09854 | 133.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997570 SIEM 8743066 230 4 | 675 | 675 | 0.08961 | 100.57 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997571 SIEM 8743066 230 3 | 675 | 675 | 0.08961 | 100.57 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 SIEM 8743066 230 2 | 559 | 643 | 0.08587 | 101.16 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 3 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 SIEM 8743066 230 2 | 559 | 643 | 0.08961 | 105.57 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | 2768 | 2768 | 0.26637 | 101.98 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | 2768 | 2768 | 0.26637 | 101.98 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.06355 | 103.48 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.06355 | 103.48 | Potential P4 Event - POI 588839_3 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08844 | 100.5 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08844 | 100.54 | Potential P4 Event - POI 511568_2 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08844 | 100.54 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08844 | 100.61 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08844 | 100.65 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.11209 | 104.83 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.11209 | 104.83 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.11209 | 104.83 | Potential P4 Event - POI 511468_11 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 515045 SEMINOL7 345 560101 SEMINOLE765 765 1 | 2768 | 2768 | 0.26201 | 101.94 | 515045 SEMINOL7 345 560101 SEMINOLE765 765 2 | Cumulative Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 515045 SEMINOL7 345 560101 SEMINOLE765 765 2 | 2768 | 2768 | 0.26201 | 101.94 | 515045 SEMINOL7 345 560101 SEMINOLE765 765 1 | Cumulative Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.07465 | 104.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.07465 | 104.3 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.07465 | 104.3 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | 2768 | 2768 | 0.26201 | 101.98 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | 2768 | 2768 | 0.26201 | 101.98 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08954 | 100.5 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08954 | 100.54 | Potential P4 Event - POI 511568_2 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08954 | 100.54 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08954 | 100.61 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.08954 | 100.65 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.09199 | 104.83 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.09199 | 104.83 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.09199 | 104.83 | Potential P4 Event - POI 511468_11 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.09644 | 103.48 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.09644 | 103.48 | Potential P4 Event - POI 588839_3 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.0795 | 125.64 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08123 | 126.36 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08123 | 126.75 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08123 | 126.75 | POI 515800_22 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08123 | 126.75 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08123 | 126.75 | Potential P4 Event - POI 560078_4 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08147 | 127.3 | Potential P4 Event - POI 515800_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.0795 | 131.15 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.08123 | 131.84 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.08123 | 132.38 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.08123 | 132.38 | POI 515800_22 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.08123 | 132.38 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.08123 | 132.38 | Potential P4 Event - POI 560078_4 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 501 | 501 | 0.08147 | 133.03 | Potential P4 Event - POI 515800_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.0795 | 125.49 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08123 | 126.12 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08123 | 126.59 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08123 | 126.59 | Potential P4 Event - POI 515800_9 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08123 | 126.59 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08123 | 126.59 | Potential P4 Event - POI 560078_4 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 510 | 510 | 0.08147 | 127.17 | Potential P4 Event - POI 515800_3 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0537 | 145.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0537 | 145.69 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 396 | 441 | 0.0583 | 102.07 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 396 | 441 | 0.0583 | 102.15 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 515045 SEMINOL7 345 560101 SEMINOLE765 765 1 | 2768 | 2768 | 0.33677 | 101.94 | 515045 SEMINOL7 345 560101 SEMINOLE765 765 2 | Cumulative Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 515045 SEMINOL7 345 560101 SEMINOLE765 765 2 | 2768 | 2768 | 0.33677 | 101.94 | 515045 SEMINOL7 345 560101 SEMINOLE765 765 1 | Cumulative Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.08236 | 127.36 | P42:345:OKGE:SB_GRNT7313:::: | Cumulative Impact | Gracemont to Minco 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.08236 | 127.36 | Potential P4 Event - POI 515800_1 | Cumulative Impact | Gracemont to Minco 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.08236 | 130.92 | P42:345:OKGE:SB_GRNT7313:::: | Cumulative Impact | Gracemont to Minco 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.08236 | 130.92 | Potential P4 Event - POI 515800_1 | Cumulative Impact | Gracemont to Minco 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.13359 | 104.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.13359 | 104.3 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.13359 | 104.3 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 385 | 385 | 0.0583 | 116.17 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 385 | 385 | 0.0583 | 116.26 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 840 | 840 | 0.08267 | 104.14 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 2 | Cumulative Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 2 | 840 | 840 | 0.08267 | 104.14 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.05198 | 111.69 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06388 | 104.58 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06392 | 104.53 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06393 | 104.87 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.57 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.57 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.58 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.58 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.58 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.79 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.85 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.85 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.88 | P13:138:EES:LC:T2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.93 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.94 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.94 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.96 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.97 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.97 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.01 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.24 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.25 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.27 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.27 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.28 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.28 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.28 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.33 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.33 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.35 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.35 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.44 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.51 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.51 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.53 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.53 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.55 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.55 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.57 | P11:25:EES:WATERF:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.57 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.57 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.85 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.85 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.94 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 107.15 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 109.59 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06396 | 104.78 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06396 | 104.78 | 659425 SD.LS-KS-MB3 345 763666 G21-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06396 | 104.78 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06398 | 104.82 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06398 | 104.82 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06398 | 104.85 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06403 | 104.35 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06404 | 104.36 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0641 | 104.88 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06417 | 105.27 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06417 | 105.27 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06421 | 105.9 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06421 | 105.92 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06425 | 105.65 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06425 | 105.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06427 | 105.74 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06433 | 105.46 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06436 | 105.08 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06452 | 105.78 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06452 | 105.79 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06452 | 105.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06465 | 106.19 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06553 | 106.98 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06647 | 108.77 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06647 | 108.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06751 | 110.98 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06894 | 114.64 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07393 | 118.23 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07417 | 118.5 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07417 | 118.5 | Potential P4 Event - POI 515800_18 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07417 | 118.56 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0759 | 119.08 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0759 | 119.96 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07709 | 107.25 | 526936 YOAKUM 7 345 764866 G20-059-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08129 | 112.74 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08201 | 134.76 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08201 | 134.76 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 3 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10299 | 123.69 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10299 | 123.94 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10316 | 117.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10316 | 120.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10316 | 122.95 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10316 | 123.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10316 | 123.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997570 SIEM 8743066 230 4 | 675 | 675 | 0.07458 | 101.53 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997571 SIEM 8743066 230 3 | 675 | 675 | 0.07458 | 101.53 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 SIEM 8743066 230 2 | 559 | 643 | 0.07147 | 102.1 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 SIEM 8743066 230 2 | 559 | 643 | 0.07458 | 106.59 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1385 | 1385 | 0.21847 | 102.96 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1385 | 1385 | 0.21847 | 102.85 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.05198 | 111.32 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06383 | 103.58 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06392 | 103.58 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06393 | 103.89 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.62 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.63 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.81 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.88 | P13:138:EES:LC:T2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.92 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.92 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.93 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.94 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.94 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.96 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.97 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 103.97 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.01 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.49 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.5 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.52 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.52 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.52 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.53 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.56 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.57 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.57 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.59 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.68 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.72 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.72 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.75 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.75 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.77 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.77 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 104.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.04 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 105.21 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 106.59 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06394 | 109.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06398 | 103.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06398 | 103.84 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06398 | 103.86 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06403 | 103.41 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06404 | 103.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0641 | 103.89 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06417 | 104.52 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06417 | 104.52 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06421 | 105.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06421 | 105.11 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06425 | 104.87 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06425 | 104.87 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06427 | 104.95 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06433 | 104.68 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06436 | 104.07 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06452 | 104.98 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06452 | 105.02 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06452 | 105.02 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06465 | 105.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06553 | 106.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06647 | 107.99 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06647 | 108 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06751 | 110.38 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.06894 | 114.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07393 | 118.07 | P42:345:OKGE:SB_GRNT7381:::: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07417 | 118.39 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07417 | 118.39 | POI 515800_23 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07417 | 118.42 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0759 | 119.12 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.0759 | 120.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.07709 | 106.48 | 526936 YOAKUM 7 345 764866 G20-059-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08129 | 112.31 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08201 | 133.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.08201 | 133.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 4 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10299 | 123.69 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10299 | 124.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10316 | 117.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10316 | 120.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10316 | 122.86 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10316 | 123.52 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 559 | 559 | 0.10316 | 123.52 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997570 SIEM 8743066 230 4 | 675 | 675 | 0.07458 | 100.57 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997571 SIEM 8743066 230 3 | 675 | 675 | 0.07458 | 100.57 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 SIEM 8743066 230 2 | 559 | 643 | 0.07147 | 101.16 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 3 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 SIEM 8743066 230 2 | 559 | 643 | 0.07458 | 105.57 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | 2768 | 2768 | 0.33677 | 101.98 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | 2768 | 2768 | 0.33677 | 101.98 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.10746 | 100.5 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.10746 | 100.54 | Potential P4 Event - POI 511568_2 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.10746 | 100.54 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.10746 | 100.61 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.10746 | 100.65 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.11214 | 104.83 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.11214 | 104.83 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.11214 | 104.83 | Potential P4 Event - POI 511468_11 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.12348 | 103.48 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 1135 | 1135 | 0.12348 | 103.48 | Potential P4 Event - POI 588839_3 | Cumulative Impact | Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 515045 SEMINOL7 345 560101 SEMINOLE765 765 1 | 2768 | 2768 | 0.49212 | 101.94 | 515045 SEMINOL7 345 560101 SEMINOLE765 765 2 | Cumulative Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 515045 SEMINOL7 345 560101 SEMINOLE765 765 2 | 2768 | 2768 | 0.49212 | 101.94 | 515045 SEMINOL7 345 560101 SEMINOLE765 765 1 | Cumulative Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.08996 | 104.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.08996 | 104.3 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.08996 | 104.3 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | 2768 | 2768 | 0.49212 | 101.98 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
Thermal | DISIS-2023-001 CF | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | 2768 | 2768 | 0.49212 | 101.98 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
Thermal | DISIS-2023-001 | 04NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2023-001 | 05NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2023-001 CF | 04NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2023-001 CF | 05NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 CF | 04NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 CF | 05NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2023-001 CF | 04ALL | 1 | 27WP | GEN-2023-174 | FROM->TO | 521022 PAOLI 2 69.0 997686 PAOLI 69.0 1 | 70 | 70 | 0.1286 | 101.49 | P12:138:WFEC:LOCO_PAOLI:::: | Cumulative Impact | Canadian Switch138 kV Terminal Upgrades Lexington - Lil Axe 138 kV Paoli - Lexington kV 138 kV Paoli 138 kV Terminal Upgrades
Thermal | DISIS-2023-001 CF | 04ALL | 1 | 27WP | GEN-2023-174 | FROM->TO | 521022 PAOLI 2 69.0 997686 PAOLI 69.0 1 | 70 | 70 | 0.13612 | 100.71 | 520822 BASELIN4 138 521023 PAOLI 4 138 1 | Cumulative Impact | Canadian Switch138 kV Terminal Upgrades Lexington - Lil Axe 138 kV Paoli - Lexington kV 138 kV Paoli 138 kV Terminal Upgrades
Thermal | DISIS-2023-001 CF | 04ALL | 1 | 27WP | GEN-2023-174 | FROM->TO | 521023 PAOLI 4 138 997686 PAOLI 69.0 1 | 70 | 70 | 0.1286 | 101.03 | P12:138:WFEC:LOCO_PAOLI:::: | Cumulative Impact | Canadian Switch138 kV Terminal Upgrades Lexington - Lil Axe 138 kV Paoli - Lexington kV 138 kV Paoli 138 kV Terminal Upgrades
Thermal | DISIS-2023-001 CF | 04ALL | 1 | 27WP | GEN-2023-174 | FROM->TO | 521023 PAOLI 4 138 997686 PAOLI 69.0 1 | 70 | 70 | 0.13612 | 100.4 | 520822 BASELIN4 138 521023 PAOLI 4 138 1 | Cumulative Impact | Canadian Switch138 kV Terminal Upgrades Lexington - Lil Axe 138 kV Paoli - Lexington kV 138 kV Paoli 138 kV Terminal Upgrades
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.86 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.26 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.51 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 126.82 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 126.37 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 327.65 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.12 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.33 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.86 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.26 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.51 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.33 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.33 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 117.38 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.12 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.0317 | 106.97 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.86 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.26 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.51 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.86 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.26 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.51 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.62 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.12 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.07907 | 104.92 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.07907 | 100.6 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.12 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.12 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.12 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 133.78 | System Intact | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.12 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.33 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.07 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.88 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 141.93 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 174.4 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.54 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 170.93 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.07 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.88 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 141.93 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 174.4 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.54 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 170.93 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.12 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.62 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.12 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.04523 | 104.92 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04523 | 100.6 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 198.99 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.51 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.78 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 133.93 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 133.52 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 326.69 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.08 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 103.92 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 198.99 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.51 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.78 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 103.92 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 103.92 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 110.38 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.08 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 198.99 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.51 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.78 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 198.99 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.51 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.78 | System Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.63 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.08 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.08012 | 107.63 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08012 | 111.96 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08012 | 103.62 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.45 | System Intact | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.08 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.08 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.08 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 122.79 | System Intact | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.08 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 103.92 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.46 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 153.98 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 143.94 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 174.4 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.68 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 170.93 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.46 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 153.98 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 143.94 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 174.4 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.68 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 170.93 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.08 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.63 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.08 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.04532 | 107.63 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.04532 | 111.96 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04532 | 103.62 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05233 | 111.32 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05233 | 110.87 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 326.21 | System Intact | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 109.99 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 109.99 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 109.99 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.45 | System Intact | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.45 | System Intact | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 111.58 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 112.31 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 111.58 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 112.31 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 111.58 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 112.31 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 111.58 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 112.31 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 109.99 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.36 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.82 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.47 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.68 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.02 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.36 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.82 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.47 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.68 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.02 | System Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 111.58 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 112.31 | System Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.06 | System Intact | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03403 | 268.3 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 228.84 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.69 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.7 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.7 | Potential P4 Event - POI 525832_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 254.88 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 254.88 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 256.63 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04339 | 220.21 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04368 | 229.23 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.47 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 233.21 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.45 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.49 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.49 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04439 | 217.65 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04442 | 217.58 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04443 | 222.92 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04444 | 218.02 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04444 | 220.36 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04446 | 215.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.72 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:IPSCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.97 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.98 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.03 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.04 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.04 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.05 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.05 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.06 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.07 | P12:EHV:EES::8SANS SOUCI%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.09 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.12 | P23:500:EAI:NBF_SAN SO~1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.12 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.16 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.17 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.18 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.18 | P13:SH902T GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.19 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.2 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.2 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.21 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.21 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | P13:GPPS#1 GSU-FUT | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.24 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.25 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.26 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.32 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.33 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.4 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.42 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.42 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.51 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.54 | P23:345:XEL:8N8 MNN | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.64 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.65 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.68 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.68 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.69 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.73 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.76 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.77 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.78 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.81 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.82 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.84 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.91 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.91 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.95 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 217.2 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 217.2 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.74 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.74 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.76 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04477 | 227.56 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.05361 | 240.63 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03254 | 123.04 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03271 | 120.07 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 119.47 | Potential P4 Event - POI 776000_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 121.67 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03282 | 118.11 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 118.84 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03303 | 118.58 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 119.14 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 119.15 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.09 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.22 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.23 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.23 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 116.72 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 116.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.1 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.5 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.13 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.15 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.16 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.38 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.38 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.39 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.39 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.41 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.41 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.42 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.42 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.44 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.44 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.46 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.46 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.49 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.49 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.79 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.79 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.01 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.01 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03376 | 120.96 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.04236 | 170.84 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03254 | 124.66 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.47 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03271 | 121.37 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 120.78 | Potential P4 Event - POI 773600_9 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 122.95 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03282 | 119.42 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 120.13 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03303 | 119.92 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 120.49 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 120.5 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.4 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.97 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.04 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.42 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.85 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.39 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.41 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.7 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.72 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.72 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.74 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.75 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.77 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.77 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.03 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.03 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.2 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.21 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03376 | 122.42 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.04236 | 175.67 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.11023 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.11023 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.11023 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.12191 | 105.43 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.12191 | 104.92 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.24563 | 117.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.24563 | 117.5 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.25112 | 109.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.25112 | 116.39 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.25112 | 116.39 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.25112 | 116.39 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.25112 | 116.4 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16214 | 111.98 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16352 | 107.59 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16352 | 112.07 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16352 | 112.07 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16352 | 112.07 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16352 | 112.07 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16352 | 112.08 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.24563 | 117.6 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.24563 | 117.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.25112 | 109.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.25112 | 115.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.25112 | 115.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.25112 | 115.68 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.25112 | 115.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531379 JONES3 115 531426 JAMESON3 115 1 | 119.5 | 148.2 | 0.05335 | 100.85 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531379 JONES3 115 531448 HOLCOMB3 115 1 | 119.5 | 148.2 | 0.05335 | 106.84 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 355 | 355 | 0.14324 | 104.63 | Potential P4 Event - POI 531449_2 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07229 | 107.56 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07229 | 107.56 | Potential P4 Event - POI 531449_1 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07418 | 101.08 | Potential P4 Event - POI 523853_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07418 | 104 | Potential P4 Event - POI 523853_0 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07418 | 108.35 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07418 | 115.93 | Potential P4 Event - POI 531449_2 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531419 DOBSON 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.12984 | 115.14 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531420 FLETCHR3 115 531440 WILLIAM3 115 1 | 99.6 | 99.6 | 0.04146 | 103.1 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 195.4 | 195.4 | 0.12984 | 131.7 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531432 PILE 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.12984 | 114.1 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 195.4 | 195.4 | 0.07649 | 113.71 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-015 | FROM->TO | 531449 HOLCOMB7 345 997448 HOLCOMB 115 1 | 336 | 358.5 | 0.27049 | 100.35 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14507 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14507 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14507 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0381 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04011 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04012 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04012 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04012 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04012 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04012 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.46 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.10474 | 103.55 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.10474 | 108.1 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 110.4 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 111.8 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.03417 | 105.44 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-033 | FROM->TO | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 187 | 211 | 0.88161 | 117.67 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-033 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 199 | 223 | 0.94153 | 116.8 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03455 | 131.03 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03455 | 131.03 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03455 | 131.05 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03455 | 131.05 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03455 | 134.18 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03455 | 134.19 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03455 | 134.31 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03455 | 134.33 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03455 | 147.24 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.03455 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03229 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.0519 | 119.64 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 104.87 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 104.9 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 104.92 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 104.92 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 104.95 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 104.95 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 104.97 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 104.97 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 104.98 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 104.98 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.19 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.19 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.21 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.22 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.22 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.22 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.23 | 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.23 | 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.24 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.24 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.24 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.25 | P13:230:EES:NINEMI:AT5 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.25 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.26 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.26 | 505522 VAN BUR5 161 773101 GEN-2023-056 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.28 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.29 | P11:230-22-18:EES:HOOKER_E | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.3 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.36 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.36 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.36 | P11:HV:EES::1ISES U1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.39 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.39 | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.4 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.41 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.41 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.42 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.45 | P11:25:EES:WATERF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.45 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.45 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.48 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.48 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.52 | P23:345:AEPW:NES CB 3417B NBTB:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.52 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.65 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.74 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.77 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.78 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.81 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.91 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.95 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 105.95 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 106.17 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 106.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 106.63 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 106.83 | 775520 G23-177-TAP 138 775521 GEN-2023-177 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 106.83 | GEN-2023-177_POI_775520_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 107.19 | 766110 GEN-2021-088 138 766111 G21-088-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 107.19 | 766114 G21-088-XFM1 34.5 766110 GEN-2021-088 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05202 | 107.19 | GEN-2021-088_POI_766111_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05203 | 106.39 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05203 | 106.93 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05203 | 107.99 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05204 | 107.08 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05206 | 107.91 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05206 | 108.87 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05211 | 107.27 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05215 | 117.77 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05215 | 118.19 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05215 | 118.5 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05225 | 119.22 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05225 | 119.52 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05225 | 119.52 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05225 | 121.22 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05225 | 122.33 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05225 | 122.34 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05225 | 129.33 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05238 | 152.16 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05238 | 156.47 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05238 | 156.47 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05238 | 156.49 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05238 | 156.54 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05238 | 156.54 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05246 | 154.13 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.16057 | 135.34 | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.0519 | 119.28 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.49 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.53 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.55 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.55 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.58 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.58 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.59 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.6 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.6 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.81 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.81 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.83 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.84 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.84 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.85 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.86 | 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.86 | 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.86 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.87 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.88 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.88 | 505522 VAN BUR5 161 773101 GEN-2023-056 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.88 | P13:230:EES:NINEMI:AT5 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.88 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.91 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.91 | P11:230-22-18:EES:HOOKER_E | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.92 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.93 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.98 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.99 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 104.99 | P11:HV:EES::1ISES U1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.02 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.02 | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.03 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.04 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.04 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.04 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.07 | P11:25:EES:WATERF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.07 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.07 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.11 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.11 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.14 | P23:345:AEPW:NES CB 3417B NBTB:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.14 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.28 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.36 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.39 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.4 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.43 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.54 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.57 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.57 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.8 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 105.9 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 106.26 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 106.46 | 775520 G23-177-TAP 138 775521 GEN-2023-177 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 106.46 | GEN-2023-177_POI_775520_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 106.82 | 766110 GEN-2021-088 138 766111 G21-088-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 106.82 | 766114 G21-088-XFM1 34.5 766110 GEN-2021-088 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05202 | 106.82 | GEN-2021-088_POI_766111_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05203 | 106.02 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05203 | 106.55 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05203 | 107.62 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05204 | 106.7 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05206 | 107.53 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05206 | 108.5 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05211 | 106.9 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05215 | 117.41 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05215 | 117.83 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05215 | 118.15 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05225 | 118.86 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05225 | 119.16 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05225 | 119.16 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05225 | 120.86 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05225 | 121.97 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05225 | 121.98 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05225 | 128.98 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05238 | 151.84 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05238 | 156.16 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05238 | 156.16 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05238 | 156.18 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05238 | 156.23 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05238 | 156.23 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05246 | 153.82 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.16057 | 134.93 | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.58 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.59 | P13:138-24:AEPW:S.W.S.-4:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.6 | P12:138:OKGE-WFEC:BKRBKR168:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.73 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.74 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.74 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.76 | Potential P4 Event - POI 764115_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.77 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.77 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.85 | 521089 WASHITA4 138 3WXFMR WASHITA 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 280.01 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 280.03 | P12:069:WFEC:ANADRKO_WASHITA:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 280.19 | 520828 BLANCHD2 69.0 521018 OU SW 2 69.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 280.38 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 280.41 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 280.41 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 280.5 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 280.5 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 280.58 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 280.58 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 285.09 | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 288.21 | 520508 CLVJCTN2 69.0 520859 COGAR 2 69.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 288.21 | P12:138:WFEC:CLVLND_SCOTT:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-035 | FROM->TO | 520810 ANADARK2 69.0 520838 CADDO 2 69.0 1 | 58 | 68 | 0.50011 | 102.3 | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03685 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03685 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03685 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.03466 | 101.6 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.03466 | 108 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04489 | 111.68 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04713 | 114.43 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05131 | 108.6 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05134 | 108.5 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.2 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.24 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.26 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.32 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.33 | 548814 SUB M-161 161 775401 GEN-2023-171 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.33 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.34 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.35 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.35 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.45 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.46 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.46 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.5 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.55 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.55 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.56 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.61 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.62 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.68 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.68 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.76 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.76 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.8 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.83 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.83 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.85 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 108.92 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 109 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 109.01 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 109.03 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 109.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 109.04 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 109.06 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 109.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 109.07 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 109.12 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 109.12 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 109.26 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0514 | 110.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05141 | 109.27 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05141 | 109.27 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05142 | 108.35 | 52614 J2261 POI 500 338156 8POWERLN_RD% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05143 | 108.33 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05143 | 108.55 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05143 | 108.55 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05143 | 108.55 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05143 | 108.57 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05144 | 108.38 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05145 | 108.33 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05147 | 108.49 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05147 | 108.5 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05147 | 110.48 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05158 | 112.5 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05158 | 112.5 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05159 | 108.97 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05162 | 108.37 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05165 | 110.48 | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05167 | 108.96 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05167 | 108.96 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05167 | 108.96 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05171 | 109.06 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05171 | 109.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05171 | 109.14 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05178 | 109.26 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05209 | 109.26 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05232 | 113.49 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05232 | 113.55 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05234 | 111.14 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05234 | 111.15 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05303 | 112.42 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05396 | 116.18 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05396 | 116.26 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05396 | 116.26 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05396 | 116.26 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05416 | 116.46 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05494 | 119.05 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06137 | 112.32 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.03908 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.46 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.13609 | 103.55 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.13609 | 108.1 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 110.4 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 111.8 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.04393 | 105.44 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.03496 | 100.08 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.03844 | 132.53 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05168 | 107.04 | P21:161:GRDA:AFTON-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05185 | 105.21 | P21:161:GRDA:MIAMI5-AFTON5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0519 | 104.66 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0519 | 105.72 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05209 | 103.83 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05229 | 105.33 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05229 | 105.33 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05258 | 102.85 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05266 | 105.05 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05275 | 107.05 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.053 | 104.15 | P12:HV:EES::5HILLTOP%:NORFORK5!:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05304 | 103.81 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05304 | 103.87 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05304 | 103.89 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05304 | 103.89 | P21:161:EES-EAI:ST_JOE_E:HILTOP_E:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05308 | 103.38 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05308 | 103.53 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05309 | 102.97 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05325 | 102.74 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05329 | 102.55 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05329 | 102.55 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0533 | 102.54 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05332 | 102.47 | 516091 OKTAHA 7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05332 | 102.51 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05332 | 102.72 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05333 | 102.69 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05334 | 102.45 | P12:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05334 | 102.6 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05335 | 102.54 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05336 | 102.46 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05336 | 102.55 | P12:345:XEL:ASAK-ECL SPS | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05336 | 102.58 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05336 | 102.61 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.42 | 655832 BLUEBUTE-MK7 115 655849 VEEDER -MK7 115 2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.46 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.47 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.48 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.48 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.49 | P13:069-161:OPPD:S1217 T1:LT::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.5 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.5 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.56 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.57 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.65 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.71 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.75 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.81 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.87 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.88 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.9 | P11:230-22-18:EES:HOOKER_E | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 102.93 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.14 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.17 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.23 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.23 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.24 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.3 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.3 | P11:HV:EES::1ISES U1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.33 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.33 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.56 | 547479 LAR382 5 161 764315 GEN-2020-088 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.87 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.87 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 103.94 | P13:161-22:AEPW:FLINTCR5:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 104.26 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 104.59 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 104.59 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 105.67 | 547498 STL439 5 161 547655 S1G439 1 13.2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 105.74 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 105.74 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 105.74 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 106.15 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 109.21 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 109.21 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05362 | 105.37 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0538 | 107.37 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0538 | 107.37 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05403 | 104.33 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05457 | 104.14 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05505 | 104.07 | P12:138:WERE:LIBE-NSES-138:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05526 | 104.17 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05543 | 103.95 | P12:345:AEPW:ONETA--7:N.E.S.-7::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05594 | 107.17 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05616 | 105.41 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05616 | 106.49 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05725 | 104.57 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06029 | 105.26 | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.061 | 113.94 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06124 | 107.94 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06605 | 119.66 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0685 | 109.33 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0685 | 109.34 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06866 | 107.37 | Potential P4 Event - POI 770500_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06866 | 107.89 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06958 | 108.25 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06958 | 108.25 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08998 | 113.64 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08998 | 113.64 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.11992 | 115.34 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-056 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03979 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-056 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03979 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-056 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03979 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-057 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03132 | 113.64 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-057 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03132 | 113.64 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03403 | 268.3 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 228.84 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.69 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.7 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.7 | Potential P4 Event - POI 525832_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 254.88 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 254.88 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 256.63 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04339 | 220.21 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04368 | 229.23 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.47 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 233.21 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.45 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.49 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.49 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04439 | 217.65 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04442 | 217.58 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04443 | 222.92 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04444 | 218.02 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04444 | 220.36 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04446 | 215.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.72 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:IPSCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.97 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.98 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.03 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.04 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.04 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.05 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.05 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.06 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.07 | P12:EHV:EES::8SANS SOUCI%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.09 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.12 | P23:500:EAI:NBF_SAN SO~1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.12 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.16 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.17 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.18 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.18 | P13:SH902T GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.19 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.2 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.2 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.21 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.21 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | P13:GPPS#1 GSU-FUT | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.24 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.25 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.26 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.32 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.33 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.4 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.42 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.42 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.51 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.54 | P23:345:XEL:8N8 MNN | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.64 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.65 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.68 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.68 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.69 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.73 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.76 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.77 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.78 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.81 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.82 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.84 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.91 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.91 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.95 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 217.2 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 217.2 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.74 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.74 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.76 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04477 | 227.56 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.05361 | 240.63 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03254 | 123.04 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03271 | 120.07 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 119.47 | Potential P4 Event - POI 776000_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 121.67 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03282 | 118.11 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 118.84 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03303 | 118.58 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 119.14 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 119.15 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.09 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.22 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.23 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.23 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 116.72 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 116.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.1 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.5 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.13 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.15 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.16 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.38 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.38 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.39 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.39 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.41 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.41 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.42 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.42 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.44 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.44 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.46 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.46 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.49 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.49 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.79 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.79 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.01 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.01 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03376 | 120.96 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.04236 | 170.84 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03254 | 124.66 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.47 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03271 | 121.37 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 120.78 | Potential P4 Event - POI 773600_9 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 122.95 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03282 | 119.42 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 120.13 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03303 | 119.92 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 120.49 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 120.5 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.4 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.97 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.04 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.42 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.85 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.39 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.41 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.7 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.72 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.72 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.74 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.75 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.77 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.77 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.03 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.03 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.2 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.21 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03376 | 122.42 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.04236 | 175.67 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-061 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06571 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-061 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06571 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-061 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06571 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-063 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.15347 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-063 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.15347 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-063 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.15347 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03884 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04077 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0408 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0408 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0408 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0408 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0408 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-064 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.0517 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-064 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.0517 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-064 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.0517 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03085 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03085 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03085 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.03178 | 101.6 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.03178 | 108 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.09904 | 105.43 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.09904 | 104.92 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22123 | 117.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22123 | 117.5 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22784 | 109.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22784 | 116.39 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22784 | 116.39 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22784 | 116.39 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22784 | 116.4 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15163 | 111.98 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15329 | 107.59 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15329 | 112.07 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15329 | 112.07 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15329 | 112.07 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15329 | 112.07 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15329 | 112.08 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22123 | 117.6 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22123 | 117.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22784 | 109.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22784 | 115.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22784 | 115.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22784 | 115.68 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22784 | 115.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.03176 | 132.53 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03311 | 105.72 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03349 | 104.66 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03364 | 105.33 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03364 | 105.33 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03373 | 103.83 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03412 | 105.05 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0346 | 102.85 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0351 | 107.04 | P21:161:GRDA:AFTON-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03515 | 102.97 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03515 | 105.21 | P21:161:GRDA:MIAMI5-AFTON5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03518 | 104.15 | P12:HV:EES::5HILLTOP%:NORFORK5!:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03526 | 103.81 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03526 | 103.87 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03526 | 103.89 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03526 | 103.89 | P21:161:EES-EAI:ST_JOE_E:HILTOP_E:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03527 | 103.38 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03527 | 103.53 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03536 | 102.74 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03542 | 102.54 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03542 | 102.55 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03542 | 102.55 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03544 | 102.47 | 516091 OKTAHA 7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03546 | 102.51 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03547 | 102.6 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03547 | 102.72 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03548 | 102.69 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03549 | 102.45 | P12:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03549 | 102.46 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0355 | 102.54 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0355 | 102.55 | P12:345:XEL:ASAK-ECL SPS | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0355 | 102.58 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0355 | 102.61 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.42 | 655832 BLUEBUTE-MK7 115 655849 VEEDER -MK7 115 2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.46 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.47 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.48 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.48 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.49 | P13:069-161:OPPD:S1217 T1:LT::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.5 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.5 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.56 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.57 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.65 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.71 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.75 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.81 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.87 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.88 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.9 | P11:230-22-18:EES:HOOKER_E | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.93 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.14 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.17 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.23 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.23 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.24 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.3 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.3 | P11:HV:EES::1ISES U1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.33 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.33 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.56 | 547479 LAR382 5 161 764315 GEN-2020-088 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.87 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.87 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.94 | P13:161-22:AEPW:FLINTCR5:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 104.26 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 104.59 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 104.59 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 105.67 | 547498 STL439 5 161 547655 S1G439 1 13.2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 105.74 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 105.74 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 105.74 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 106.15 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 109.21 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 109.21 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03554 | 102.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03571 | 107.05 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0358 | 104.07 | P12:138:WERE:LIBE-NSES-138:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03598 | 105.37 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03607 | 104.33 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03622 | 107.37 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03622 | 107.37 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03644 | 104.14 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03719 | 104.17 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03779 | 107.17 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03804 | 105.41 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03804 | 106.49 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03918 | 104.57 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03964 | 103.95 | P12:345:AEPW:ONETA--7:N.E.S.-7::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04124 | 113.94 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04162 | 105.26 | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04228 | 107.94 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04546 | 119.66 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.063 | 113.64 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.063 | 113.64 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0671 | 107.37 | Potential P4 Event - POI 770500_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0671 | 107.89 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06849 | 109.33 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06849 | 109.34 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06958 | 108.25 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06958 | 108.25 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08764 | 115.34 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.03176 | 132.53 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03311 | 105.72 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03349 | 104.66 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03364 | 105.33 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03364 | 105.33 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03373 | 103.83 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03412 | 105.05 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0346 | 102.85 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0351 | 107.04 | P21:161:GRDA:AFTON-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03515 | 102.97 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03515 | 105.21 | P21:161:GRDA:MIAMI5-AFTON5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03518 | 104.15 | P12:HV:EES::5HILLTOP%:NORFORK5!:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03526 | 103.81 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03526 | 103.87 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03526 | 103.89 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03526 | 103.89 | P21:161:EES-EAI:ST_JOE_E:HILTOP_E:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03527 | 103.38 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03527 | 103.53 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03536 | 102.74 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03542 | 102.54 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03542 | 102.55 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03542 | 102.55 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03544 | 102.47 | 516091 OKTAHA 7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03546 | 102.51 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03547 | 102.6 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03547 | 102.72 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03548 | 102.69 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03549 | 102.45 | P12:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03549 | 102.46 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0355 | 102.54 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0355 | 102.55 | P12:345:XEL:ASAK-ECL SPS | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0355 | 102.58 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0355 | 102.61 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.42 | 655832 BLUEBUTE-MK7 115 655849 VEEDER -MK7 115 2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.46 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.47 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.48 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.48 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.49 | P13:069-161:OPPD:S1217 T1:LT::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.5 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.5 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.56 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.57 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.65 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.71 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.75 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.81 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.87 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.88 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.9 | P11:230-22-18:EES:HOOKER_E | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 102.93 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.14 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.17 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.23 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.23 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.24 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.3 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.3 | P11:HV:EES::1ISES U1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.33 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.33 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.56 | 547479 LAR382 5 161 764315 GEN-2020-088 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.87 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.87 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 103.94 | P13:161-22:AEPW:FLINTCR5:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 104.26 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 104.59 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 104.59 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 105.67 | 547498 STL439 5 161 547655 S1G439 1 13.2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 105.74 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 105.74 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 105.74 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 106.15 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 109.21 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03552 | 109.21 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03554 | 102.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03571 | 107.05 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0358 | 104.07 | P12:138:WERE:LIBE-NSES-138:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03598 | 105.37 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03607 | 104.33 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03622 | 107.37 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03622 | 107.37 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03644 | 104.14 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03719 | 104.17 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03779 | 107.17 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03804 | 105.41 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03804 | 106.49 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03918 | 104.57 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03964 | 103.95 | P12:345:AEPW:ONETA--7:N.E.S.-7::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04124 | 113.94 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04162 | 105.26 | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04228 | 107.94 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04546 | 119.66 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.063 | 113.64 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.063 | 113.64 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0671 | 107.37 | Potential P4 Event - POI 770500_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0671 | 107.89 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06849 | 109.33 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06849 | 109.34 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06958 | 108.25 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06958 | 108.25 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08764 | 115.34 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-085 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03605 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-085 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03605 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-085 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03605 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 | 318.7 | 318.7 | 0.06833 | 104.57 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.52291 | 124.79 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.53269 | 139.96 | Potential P4 Event - POI 762216_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.53269 | 139.96 | Potential P4 Event - POI 762467_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.53269 | 141.71 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.53875 | 117.45 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.54158 | 120.41 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.54158 | 120.45 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.54158 | 120.45 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.54158 | 120.45 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.54158 | 120.65 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55012 | 110.94 | P12:115:SPS:T67_1_HAPPY_KRESS:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55259 | 109.62 | P12:115:SPS:T04_1_TRABLNC_CASTRO:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55456 | 109.41 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55524 | 110.5 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55524 | 110.53 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55524 | 110.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.5553 | 110.41 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55653 | 113.18 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55653 | 113.18 | Potential P4 Event - POI 514801_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55653 | 113.23 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55665 | 108.47 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55701 | 108.9 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55701 | 110.77 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55755 | 106.93 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55755 | 108.11 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55755 | 108.15 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55757 | 106.86 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55762 | 106.77 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55763 | 106.72 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.34 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.61 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.61 | 52614 J2261 POI 500 338156 8POWERLN_RD% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.61 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.61 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.61 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.62 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.62 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.65 | 539800 CLARKCOUNTY7 345 763890 GEN-2019-058 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.65 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.65 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.66 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.66 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.66 | P23:500:EES:PERVIL:R9872 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.67 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.67 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.67 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.67 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.67 | P11:20:AMMO:1LAB G1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.67 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.67 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.68 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.68 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.69 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.7 | P13:SH902T GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.7 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.71 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.71 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.71 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.72 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.73 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.73 | P13:GPPS#1 GSU-FUT | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.75 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.78 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.78 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.79 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.82 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.83 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.83 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.88 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.88 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.89 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.9 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.9 | P23:345:XEL:8N8 MNN | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.91 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.95 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.95 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.97 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.98 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 106.99 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.03 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.06 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.06 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.07 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.07 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.08 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.08 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.09 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.33 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.44 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.44 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.47 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 107.47 | GEN-2023-015_POI_772280_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55764 | 110.22 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13836 | 101.6 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13836 | 108 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.088 | 105.43 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.088 | 104.92 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.21399 | 117.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.21399 | 117.5 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22501 | 109.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22501 | 116.39 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22501 | 116.39 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22501 | 116.39 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.22501 | 116.4 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15079 | 111.98 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15357 | 107.59 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15357 | 112.07 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15357 | 112.07 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15357 | 112.07 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15357 | 112.07 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15357 | 112.08 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.21399 | 117.6 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.21399 | 117.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22501 | 109.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22501 | 115.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22501 | 115.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22501 | 115.68 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.22501 | 115.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09698 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09698 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09698 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.12144 | 105.43 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.12144 | 104.92 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.2448 | 117.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.2448 | 117.5 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.2499 | 109.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.2499 | 116.39 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.2499 | 116.39 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.2499 | 116.39 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.2499 | 116.4 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16143 | 111.98 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16272 | 107.59 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16272 | 112.07 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16272 | 112.07 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16272 | 112.07 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16272 | 112.07 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16272 | 112.08 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.2448 | 117.6 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.2448 | 117.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.2499 | 109.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.2499 | 115.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.2499 | 115.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.2499 | 115.68 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.2499 | 115.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03664 | 103.42 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03664 | 103.42 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03664 | 103.6 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.04677 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04753 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04753 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04909 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05184 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05207 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05207 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05681 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.03015 | 135.17 | Potential P4 Event - POI 515375_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-100 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.03015 | 135.17 | Potential P4 Event - POI 515407_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48307 | 103.42 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48307 | 103.42 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48307 | 103.6 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06049 | 119.05 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0684 | 116.18 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0684 | 116.26 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0684 | 116.26 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0684 | 116.26 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07197 | 116.46 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.08954 | 110.48 | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0916 | 112.42 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09407 | 111.14 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09407 | 111.15 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09771 | 131.03 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09771 | 131.03 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09771 | 131.05 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09771 | 131.05 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09771 | 134.18 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09771 | 134.19 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09771 | 134.31 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09771 | 134.33 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09771 | 147.24 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09977 | 109.27 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09977 | 109.27 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09983 | 114.43 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10009 | 108.5 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10018 | 108.6 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10026 | 109.06 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10026 | 109.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10026 | 109.14 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10031 | 112.32 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10032 | 109.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.2 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.24 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.26 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.32 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.33 | 548814 SUB M-161 161 775401 GEN-2023-171 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.33 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.33 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.34 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.35 | 52614 J2261 POI 500 338156 8POWERLN_RD% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.35 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.35 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.45 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.46 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.46 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.5 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.55 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.55 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.55 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.55 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.55 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.56 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.57 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.61 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.62 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.68 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.68 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.76 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.76 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.8 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.83 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.83 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.85 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 108.92 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 109 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 109.01 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 109.03 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 109.04 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 109.06 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 109.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 109.07 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 109.12 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 109.12 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 109.26 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 110.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10033 | 110.48 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10034 | 108.33 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10034 | 108.38 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10034 | 108.49 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10034 | 108.5 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10035 | 108.37 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10035 | 108.96 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10035 | 108.96 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10035 | 108.96 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10035 | 108.97 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10037 | 109.26 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1004 | 109.26 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10248 | 111.68 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10319 | 113.49 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10319 | 113.55 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.14279 | 112.5 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.14279 | 112.5 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.09771 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03664 | 103.42 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03664 | 103.42 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03664 | 103.6 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.04677 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04753 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04753 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04909 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05184 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05207 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05207 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05681 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.03015 | 135.17 | Potential P4 Event - POI 515375_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-102 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.03015 | 135.17 | Potential P4 Event - POI 515407_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.08108 | 105.43 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.08108 | 104.92 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05432 | 103.42 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05432 | 103.42 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05432 | 103.6 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 514898 CIMARON4 138 997829 CIMARON1 138 1 | 478 | 478 | 0.03413 | 100.86 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 514901 CIMARON7 345 997829 CIMARON1 138 1 | 478 | 478 | 0.03413 | 104.58 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.21316 | 117.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.21316 | 117.5 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.23787 | 109.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.23787 | 116.39 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.23787 | 116.39 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.23787 | 116.39 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.23787 | 116.4 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.15595 | 111.98 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16218 | 107.59 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16218 | 112.07 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16218 | 112.07 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16218 | 112.07 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16218 | 112.07 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.16218 | 112.08 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.21316 | 117.6 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.21316 | 117.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.23787 | 109.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.23787 | 115.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.23787 | 115.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.23787 | 115.68 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.23787 | 115.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.03119 | 100.26 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.03119 | 100.47 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.03119 | 100.47 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.03119 | 100.94 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.0317 | 106.67 | 520882 DOVERSW4 138 762493 GEN-2018-011 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.0317 | 106.67 | 762494 G18-011-XFM1 34.5 762493 GEN-2018-011 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.0317 | 106.67 | GEN-2018-011_POI_520882_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.0321 | 114.23 | P12:138:OKGE-WFEC:BKRBKR98:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.0321 | 114.23 | P12:138:WFEC:ELRENO_JENSEN:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.03288 | 101.53 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.03294 | 102.36 | Potential P4 Event - POI 539801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.0336 | 109.6 | P12:138:OKGE-WFEC:BKRBKR81:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.0336 | 109.6 | P12:138:WFEC:MOORELND_CLEOCRNR:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.0336 | 109.76 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.0339 | 108.56 | Potential P4 Event - POI 539801_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.04152 | 135.17 | Potential P4 Event - POI 515375_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.04152 | 135.17 | Potential P4 Event - POI 515407_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-104 | FROM->TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 74 | 83 | 0.08191 | 105.04 | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-132 | FROM->TO | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 205 | 205 | 1 | 107.58 | 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | TDF Impact | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-134 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.18488 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-134 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.18488 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-134 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.18488 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-134 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13442 | 101.6 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-134 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13442 | 108 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.43347 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.43347 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.43347 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-135 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03017 | 109.26 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03403 | 268.3 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 228.84 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.69 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.7 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.7 | Potential P4 Event - POI 525832_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 254.88 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 254.88 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 256.63 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04339 | 220.21 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04368 | 229.23 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.47 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 233.21 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.45 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.49 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.49 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04439 | 217.65 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04442 | 217.58 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04443 | 222.92 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04444 | 218.02 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04444 | 220.36 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04446 | 215.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.72 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:IPSCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.97 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.98 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.03 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.04 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.04 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.05 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.05 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.06 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.07 | P12:EHV:EES::8SANS SOUCI%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.09 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.12 | P23:500:EAI:NBF_SAN SO~1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.12 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.16 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.17 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.18 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.18 | P13:SH902T GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.19 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.2 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.2 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.21 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.21 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | P13:GPPS#1 GSU-FUT | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.24 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.25 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.26 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.32 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.33 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.4 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.42 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.42 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.51 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.54 | P23:345:XEL:8N8 MNN | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.64 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.65 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.68 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.68 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.69 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.73 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.76 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.77 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.78 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.81 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.82 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.84 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.91 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.91 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.95 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 217.2 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 217.2 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.74 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.74 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.76 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04477 | 227.56 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.05361 | 240.63 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03254 | 123.04 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03271 | 120.07 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 119.47 | Potential P4 Event - POI 776000_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 121.67 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03282 | 118.11 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 118.84 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03303 | 118.58 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 119.14 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 119.15 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.09 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.22 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.23 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.23 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 116.72 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 116.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.1 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.5 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.13 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.15 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.16 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.38 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.38 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.39 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.39 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.41 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.41 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.42 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.42 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.44 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.44 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.46 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.46 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.49 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.49 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.79 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.79 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.01 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.01 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03376 | 120.96 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.04236 | 170.84 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03254 | 124.66 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.47 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03271 | 121.37 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 120.78 | Potential P4 Event - POI 773600_9 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 122.95 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03282 | 119.42 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 120.13 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03303 | 119.92 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 120.49 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 120.5 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.4 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.97 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.04 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.42 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.85 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.39 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.41 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.7 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.72 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.72 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.74 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.75 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.77 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.77 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.03 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.03 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.2 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.21 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03376 | 122.42 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.04236 | 175.67 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03403 | 268.3 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 228.84 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.69 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.7 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04238 | 237.7 | Potential P4 Event - POI 525832_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 254.88 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 254.88 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04336 | 256.63 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04339 | 220.21 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04368 | 229.23 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.47 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 232.53 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04379 | 233.21 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.45 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.49 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04436 | 220.49 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04439 | 217.65 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04442 | 217.58 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04443 | 222.92 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04444 | 218.02 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04444 | 220.36 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04446 | 215.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.72 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:IPSCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.97 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 214.98 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.03 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.04 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.04 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.05 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.05 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.06 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.07 | P12:EHV:EES::8SANS SOUCI%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.09 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.1 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.11 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.12 | P23:500:EAI:NBF_SAN SO~1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.12 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.15 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.16 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.17 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.18 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.18 | P13:SH902T GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.19 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.2 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.2 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.21 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.21 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.23 | P13:GPPS#1 GSU-FUT | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.24 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.25 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.26 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.32 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.33 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.4 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.42 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.42 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.51 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.54 | P23:345:XEL:8N8 MNN | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.6 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.64 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.65 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.68 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.68 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.69 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.73 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.76 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.77 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.78 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.81 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.82 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.84 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.91 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.91 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 215.95 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 217.2 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 217.2 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.74 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.74 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04447 | 226.76 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04477 | 227.56 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.05361 | 240.63 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03254 | 123.04 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 122.87 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03271 | 120.07 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 119.47 | Potential P4 Event - POI 776000_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 121.67 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03282 | 118.11 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 118.84 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03303 | 118.58 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 119.14 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 119.15 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.09 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.22 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.23 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 117.23 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 116.72 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 116.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.1 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.5 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.13 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.15 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.16 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.37 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.38 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.38 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.39 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.39 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.4 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.41 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.41 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.42 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.42 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.43 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.44 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.44 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.45 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.46 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.46 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.49 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.49 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.79 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 116.79 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.01 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.01 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03376 | 120.96 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.04236 | 170.84 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03254 | 124.66 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.47 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03262 | 124.48 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03271 | 121.37 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 120.78 | Potential P4 Event - POI 773600_9 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03279 | 122.95 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03282 | 119.42 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 120.13 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03303 | 119.92 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 120.49 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03304 | 120.5 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.4 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03311 | 118.48 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 117.97 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.04 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.42 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03312 | 118.85 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.37 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.39 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.41 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.62 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.63 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.64 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.67 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.68 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.69 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.7 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.71 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.72 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.72 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.73 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.74 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.75 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.77 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 117.77 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.03 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.03 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.2 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03313 | 118.21 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03376 | 122.42 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.04236 | 175.67 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 542965 W.GRDNR7 345 997213 WEST GARDN11 161 11 | 535 | 535 | 0.08514 | 100.64 | Potential P4 Event - POI 542940_3 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 542965 W.GRDNR7 345 997213 WEST GARDN11 161 11 | 535 | 535 | 0.08514 | 104.21 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 542965 W.GRDNR7 345 997213 WEST GARDN11 161 11 | 535 | 535 | 0.10859 | 106.73 | Potential P4 Event - POI 542965_4 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.04985 | 105.22 | Potential P4 Event - POI 542940_3 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.04985 | 108.05 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.06043 | 104.08 | Potential P4 Event - POI 542965_4 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 | 311 | 334 | 0.03981 | 101.96 | Potential P4 Event - POI 542965_4 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 997213 WEST GARDN11 161 11 | 535 | 535 | 0.08514 | 103.3 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 997213 WEST GARDN11 161 11 | 535 | 535 | 0.10859 | 105.67 | Potential P4 Event - POI 542965_4 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 311 | 334 | 0.13717 | 107.86 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1 | 311 | 334 | 0.03433 | 102.28 | 543036 OLATHE 5 161 543045 SWITZER5 161 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.10589 | 103.32 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.107 | 103.31 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.107 | 103.31 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.10798 | 103.35 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.10798 | 103.35 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11311 | 100.81 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.10589 | 111.21 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.107 | 111.2 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.107 | 111.2 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.10798 | 111.26 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.10798 | 111.26 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.10983 | 105.69 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11311 | 108.49 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05831 | 103.98 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06855 | 109.45 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06855 | 111.27 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06855 | 112.45 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0706 | 132.71 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07087 | 132.7 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07087 | 132.7 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07142 | 132.74 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07142 | 132.74 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07172 | 107.22 | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07172 | 108.31 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07225 | 128.55 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0733 | 129.99 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.10589 | 120.95 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.107 | 120.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.107 | 120.93 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.10798 | 120.96 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.10798 | 120.96 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.10983 | 115.79 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11311 | 118.28 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0523 | 107.98 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05258 | 115.96 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.48 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.49 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.73 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.73 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.74 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.74 | P13:230:EES:NINEMI:AT5 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.74 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.74 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.75 | 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.75 | 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.75 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.76 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.76 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.77 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.77 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.77 | P11:230-22-18:EES:HOOKER_E | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.79 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.81 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.84 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.85 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.85 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.85 | P11:HV:EES::1ISES U1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.86 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.86 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.87 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.87 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.87 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.87 | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.88 | P11:25:EES:WATERF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.88 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.89 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.98 | P23:345:AEPW:NES CB 3417B NBTB:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 101.98 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 102.18 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 102.2 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 102.38 | 775520 G23-177-TAP 138 775521 GEN-2023-177 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 102.59 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 102.6 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 102.6 | GEN-2022-238_POI_515055_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 102.86 | 774660 G23-134-TAP 138 774661 GEN-2023-134 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 102.86 | 774661 GEN-2023-134 138 774662 G23-134XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05347 | 102.86 | GEN-2023-134_POI_774660_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05348 | 102.17 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05348 | 102.19 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05348 | 102.22 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05349 | 101.97 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05349 | 101.97 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0535 | 102.3 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0535 | 102.33 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0535 | 102.33 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05351 | 102.62 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05361 | 102.92 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05373 | 103.5 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05374 | 104.41 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.054 | 103.27 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05401 | 103.24 | P12:138:OKGE:BKRBKR95:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0579 | 108.79 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05831 | 114.46 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05831 | 114.46 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05831 | 116.93 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05831 | 116.95 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05831 | 123.39 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06204 | 111.45 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06855 | 128.49 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06855 | 130.42 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06855 | 131.64 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0706 | 152.5 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07087 | 152.49 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07087 | 152.49 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07142 | 152.54 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07142 | 152.54 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07172 | 126.17 | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07172 | 127.26 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0733 | 149.75 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07677 | 148.24 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.10589 | 108.47 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.107 | 108.46 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.107 | 108.46 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.10798 | 108.49 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.10798 | 108.49 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.10983 | 103.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11311 | 105.9 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34154 | 112.5 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34154 | 112.5 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34436 | 108.33 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34436 | 108.38 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34436 | 110.48 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.2 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.24 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.26 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.32 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.33 | 548814 SUB M-161 161 775401 GEN-2023-171 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.33 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.33 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.34 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.35 | 52614 J2261 POI 500 338156 8POWERLN_RD% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.35 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.35 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.45 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.46 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.46 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.5 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.55 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.55 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.55 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.55 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.55 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.56 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.57 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.61 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.62 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.68 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.68 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.76 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.76 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.8 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.83 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.83 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.85 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 108.92 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 109 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 109.01 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 109.03 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 109.04 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 109.06 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 109.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 109.07 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 109.12 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 109.12 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 109.26 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34437 | 110.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34438 | 109.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34439 | 108.49 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34439 | 108.5 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34444 | 108.97 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34445 | 108.37 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34445 | 108.6 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34447 | 108.96 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34447 | 108.96 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34447 | 108.96 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34455 | 108.5 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34455 | 109.26 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34463 | 109.27 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34463 | 109.27 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34464 | 109.26 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34474 | 109.06 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34474 | 109.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34474 | 109.14 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34497 | 110.48 | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34727 | 111.14 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34727 | 111.15 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34972 | 112.42 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35144 | 116.18 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35144 | 116.26 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35144 | 116.26 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35144 | 116.26 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3526 | 116.46 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35459 | 119.05 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35675 | 112.32 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35826 | 114.43 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.36398 | 111.68 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.37177 | 113.49 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.37177 | 113.55 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4247 | 131.03 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4247 | 131.03 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4247 | 131.05 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4247 | 131.05 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4247 | 134.18 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4247 | 134.19 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4247 | 134.31 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4247 | 134.33 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4247 | 147.24 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.452 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03485 | 104.86 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03485 | 106.26 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03485 | 109.17 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03351 | 100.6 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03351 | 102.09 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03351 | 103.17 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03086 | 100.15 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03086 | 100.34 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03086 | 100.34 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03086 | 100.86 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03086 | 100.86 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03086 | 101.61 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03086 | 101.61 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0322 | 100.12 | P42:345:OKGE:SB_CION7383:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03351 | 111.19 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03351 | 112.68 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03351 | 113.76 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515135 SUNNYSD4 138 997799 SUNNYSD3 138 3 | 330 | 330 | 0.03501 | 103.63 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.2682 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.2682 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.26976 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.27274 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.27274 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.27344 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.29194 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 997799 SUNNYSD3 138 3 | 330 | 330 | 0.03501 | 102.54 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.19514 | 112.08 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.19544 | 112.07 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.19544 | 112.07 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.19659 | 112.07 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.19659 | 112.07 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.19814 | 107.59 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.20461 | 111.98 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08431 | 101.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08431 | 101.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08431 | 103.44 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08431 | 103.45 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08431 | 108.9 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08984 | 104.09 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08984 | 104.14 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08984 | 104.42 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.09141 | 107.79 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.09141 | 110.27 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.09235 | 106.34 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.09235 | 110.29 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10033 | 140.49 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10062 | 140.48 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10062 | 140.48 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10132 | 140.5 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10132 | 140.5 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10233 | 136.23 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10453 | 138.47 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08431 | 105.14 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08984 | 100.38 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08984 | 100.42 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08984 | 100.71 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.09141 | 104.06 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.09141 | 106.53 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.09235 | 102.65 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.09235 | 106.58 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10033 | 136.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10062 | 136.66 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10062 | 136.66 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10132 | 136.68 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10132 | 136.68 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10233 | 132.43 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10453 | 134.65 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10211 | 103.05 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10249 | 103.04 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10249 | 103.04 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10331 | 103.05 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10331 | 103.05 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.107 | 101.15 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10211 | 110.29 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10249 | 110.27 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10249 | 110.27 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10331 | 110.28 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10331 | 110.28 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10453 | 106.66 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.107 | 108.36 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.07076 | 106.05 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08125 | 120.19 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08132 | 120.18 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08132 | 120.18 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08203 | 120.19 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08203 | 120.19 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08292 | 116.29 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08459 | 117.91 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.07076 | 103.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08125 | 117.7 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08132 | 117.69 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08132 | 117.69 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08203 | 117.7 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08203 | 117.7 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08292 | 113.81 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08459 | 115.42 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10211 | 117.94 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10249 | 117.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10249 | 117.93 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10331 | 117.93 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10331 | 117.93 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10453 | 114.28 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.107 | 116 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10211 | 116.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10249 | 116.1 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10249 | 116.1 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10331 | 116.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10331 | 116.1 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10453 | 112.46 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.107 | 114.17 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10211 | 116.1 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10249 | 116.09 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10249 | 116.09 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10331 | 116.09 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10331 | 116.09 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10453 | 112.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.107 | 114.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.21677 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.21677 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.21677 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.05173 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.12366 | 104.86 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.12366 | 106.26 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.12366 | 109.17 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.12209 | 100.6 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.12209 | 102.09 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.12209 | 103.17 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.08705 | 108.99 | P12:138:OKGE:BKRBKR125:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09157 | 101.75 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09157 | 101.75 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09157 | 102.65 | 775341 GEN-2023-168 138 775342 G23-168XFMR1 34.5 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09157 | 102.65 | GEN-2023-168_POI_514922_Generator_outage | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09394 | 100.15 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09394 | 100.34 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09394 | 100.34 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09394 | 100.86 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09394 | 100.86 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09394 | 101.61 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09394 | 101.61 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09539 | 102.35 | Potential P4 Event - POI 515497_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09616 | 100.12 | P42:345:OKGE:SB_CION7383:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.12209 | 111.19 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.12209 | 112.68 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.12209 | 113.76 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05812 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05812 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05969 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06081 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06266 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06266 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06669 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.07932 | 103.32 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08042 | 103.31 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08042 | 103.31 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.0814 | 103.35 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.0814 | 103.35 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08976 | 100.81 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.07932 | 111.21 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08042 | 111.2 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08042 | 111.2 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.0814 | 111.26 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.0814 | 111.26 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08325 | 105.69 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08976 | 108.49 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0468 | 132.71 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04707 | 132.7 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04707 | 132.7 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04763 | 132.74 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04763 | 132.74 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04845 | 128.55 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05054 | 129.99 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.07932 | 120.95 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08042 | 120.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08042 | 120.93 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.0814 | 120.96 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.0814 | 120.96 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08325 | 115.79 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08976 | 118.28 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03341 | 125.81 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03365 | 125.8 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03365 | 125.8 | Potential P4 Event - POI 514801_4 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03403 | 125.87 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03403 | 125.87 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03818 | 125.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0468 | 152.5 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04707 | 152.49 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04707 | 152.49 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04763 | 152.54 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04763 | 152.54 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05054 | 149.75 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05778 | 148.24 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03341 | 116.31 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03365 | 116.3 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03365 | 116.3 | Potential P4 Event - POI 514801_3 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03403 | 116.37 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03403 | 116.37 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03818 | 115.72 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.07932 | 108.47 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08042 | 108.46 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08042 | 108.46 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.0814 | 108.49 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.0814 | 108.49 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08325 | 103.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08976 | 105.9 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49546 | 108.33 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49546 | 108.35 | 52614 J2261 POI 500 338156 8POWERLN_RD% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49546 | 108.38 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49546 | 110.48 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.2 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.24 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.26 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.32 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.33 | 548814 SUB M-161 161 775401 GEN-2023-171 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.33 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.33 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.34 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.35 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.35 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.45 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.46 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.46 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.5 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.55 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.55 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.55 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.55 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.55 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.56 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.57 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.61 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.62 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.68 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.68 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.76 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.76 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.8 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.83 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.83 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.85 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.92 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.01 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.03 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.04 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.06 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.07 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.12 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.12 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.26 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 110.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49549 | 108.49 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49549 | 108.5 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49553 | 108.97 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49554 | 108.37 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49556 | 108.6 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49556 | 108.96 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49556 | 108.96 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49556 | 108.96 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49564 | 109.26 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49566 | 108.5 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49572 | 109.26 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49576 | 109.27 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49576 | 109.27 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49585 | 109.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49585 | 109.14 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49586 | 109.06 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4962 | 110.48 | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49866 | 111.14 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49866 | 111.15 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50129 | 112.42 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50309 | 112.5 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50309 | 112.5 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50365 | 111.68 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50367 | 116.18 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50367 | 116.26 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50367 | 116.26 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50367 | 116.26 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50481 | 116.46 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50711 | 113.49 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50711 | 113.55 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50719 | 119.05 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50856 | 112.32 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.51174 | 114.43 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 131.03 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 131.03 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 131.05 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 131.05 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 134.18 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 134.19 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 134.31 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 134.33 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 147.24 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.61783 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03086 | 104.86 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03086 | 106.26 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03086 | 109.17 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03311 | 100.6 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03311 | 102.09 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03311 | 103.17 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03113 | 102.35 | Potential P4 Event - POI 515497_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 100.15 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 100.34 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 100.34 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 100.86 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 100.86 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 101.61 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 101.61 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03311 | 111.19 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03311 | 112.68 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03311 | 113.76 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03494 | 100.12 | P42:345:OKGE:SB_CION7383:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515135 SUNNYSD4 138 997799 SUNNYSD3 138 3 | 330 | 330 | 0.04417 | 103.63 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.34638 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.34638 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.34794 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.34831 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35092 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35092 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.38459 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 997799 SUNNYSD3 138 3 | 330 | 330 | 0.04417 | 102.54 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.27123 | 116.4 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 116.39 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 116.39 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 116.39 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.27989 | 109.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.33073 | 117.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.33073 | 117.5 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09381 | 112.08 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09411 | 112.07 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09411 | 112.07 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09526 | 112.07 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09526 | 112.07 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09681 | 107.59 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.10964 | 111.98 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.27123 | 115.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 115.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 115.68 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 115.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.27989 | 109.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.33073 | 117.6 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.33073 | 117.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03238 | 104.09 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03238 | 104.14 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03238 | 104.42 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03289 | 107.79 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03289 | 110.27 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03328 | 106.34 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03328 | 110.29 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03401 | 101.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03401 | 101.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03401 | 103.44 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03401 | 103.45 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03401 | 108.9 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05852 | 140.49 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05881 | 140.48 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05881 | 140.48 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05951 | 140.5 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05951 | 140.5 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06052 | 136.23 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06489 | 138.47 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03238 | 100.38 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03238 | 100.42 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03238 | 100.71 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03289 | 104.06 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03289 | 106.53 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03328 | 102.65 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03328 | 106.58 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03401 | 105.14 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05852 | 136.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05881 | 136.66 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05881 | 136.66 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05951 | 136.68 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05951 | 136.68 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06052 | 132.43 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06489 | 134.65 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.06929 | 103.05 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.06967 | 103.04 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.06967 | 103.04 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.0705 | 103.05 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.0705 | 103.05 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07662 | 101.15 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.06929 | 110.29 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.06967 | 110.27 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.06967 | 110.27 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.0705 | 110.28 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.0705 | 110.28 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07172 | 106.66 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07662 | 108.36 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04079 | 106.05 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05835 | 120.19 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05843 | 120.18 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05843 | 120.18 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05914 | 120.19 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05914 | 120.19 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06003 | 116.29 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06334 | 117.91 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04079 | 103.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05835 | 117.7 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05843 | 117.69 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05843 | 117.69 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05914 | 117.7 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05914 | 117.7 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.06003 | 113.81 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.06334 | 115.42 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.06929 | 117.94 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.06967 | 117.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.06967 | 117.93 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.0705 | 117.93 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.0705 | 117.93 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07172 | 114.28 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07662 | 116 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06929 | 116.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06967 | 116.1 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06967 | 116.1 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0705 | 116.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0705 | 116.1 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07172 | 112.46 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07662 | 114.17 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06929 | 116.1 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06967 | 116.09 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06967 | 116.09 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0705 | 116.09 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0705 | 116.09 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07172 | 112.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07662 | 114.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.07932 | 103.32 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08042 | 103.31 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08042 | 103.31 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.0814 | 103.35 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.0814 | 103.35 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08976 | 100.81 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.07932 | 111.21 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08042 | 111.2 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08042 | 111.2 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.0814 | 111.26 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.0814 | 111.26 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08325 | 105.69 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08976 | 108.49 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0468 | 132.71 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04707 | 132.7 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04707 | 132.7 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04763 | 132.74 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04763 | 132.74 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04845 | 128.55 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05054 | 129.99 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.07932 | 120.95 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08042 | 120.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08042 | 120.93 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.0814 | 120.96 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.0814 | 120.96 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08325 | 115.79 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08976 | 118.28 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03341 | 125.81 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03365 | 125.8 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03365 | 125.8 | Potential P4 Event - POI 514801_4 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03403 | 125.87 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03403 | 125.87 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03818 | 125.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0468 | 152.5 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04707 | 152.49 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04707 | 152.49 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04763 | 152.54 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04763 | 152.54 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05054 | 149.75 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05778 | 148.24 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03341 | 116.31 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03365 | 116.3 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03365 | 116.3 | Potential P4 Event - POI 514801_3 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03403 | 116.37 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03403 | 116.37 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03818 | 115.72 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.07932 | 108.47 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08042 | 108.46 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08042 | 108.46 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.0814 | 108.49 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.0814 | 108.49 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08325 | 103.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08976 | 105.9 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49546 | 108.33 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49546 | 108.35 | 52614 J2261 POI 500 338156 8POWERLN_RD% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49546 | 108.38 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49546 | 110.48 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.2 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.24 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.26 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.32 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.33 | 548814 SUB M-161 161 775401 GEN-2023-171 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.33 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.33 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.34 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.35 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.35 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.45 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.46 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.46 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.5 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.55 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.55 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.55 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.55 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.55 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.56 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.57 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.61 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.62 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.68 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.68 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.76 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.76 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.8 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.83 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.83 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.85 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 108.92 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.01 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.03 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.04 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.06 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.07 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.12 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.12 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 109.26 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49547 | 110.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49549 | 108.49 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49549 | 108.5 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49553 | 108.97 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49554 | 108.37 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49556 | 108.6 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49556 | 108.96 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49556 | 108.96 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49556 | 108.96 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49564 | 109.26 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49566 | 108.5 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49572 | 109.26 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49576 | 109.27 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49576 | 109.27 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49585 | 109.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49585 | 109.14 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49586 | 109.06 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4962 | 110.48 | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49866 | 111.14 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49866 | 111.15 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50129 | 112.42 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50309 | 112.5 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50309 | 112.5 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50365 | 111.68 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50367 | 116.18 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50367 | 116.26 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50367 | 116.26 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50367 | 116.26 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50481 | 116.46 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50711 | 113.49 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50711 | 113.55 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50719 | 119.05 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50856 | 112.32 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.51174 | 114.43 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 131.03 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 131.03 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 131.05 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 131.05 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 134.18 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 134.19 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 134.31 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 134.33 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59053 | 147.24 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.61783 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03086 | 104.86 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03086 | 106.26 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03086 | 109.17 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03311 | 100.6 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03311 | 102.09 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03311 | 103.17 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03113 | 102.35 | Potential P4 Event - POI 515497_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 100.15 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 100.34 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 100.34 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 100.86 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 100.86 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 101.61 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03296 | 101.61 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03311 | 111.19 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03311 | 112.68 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03311 | 113.76 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03494 | 100.12 | P42:345:OKGE:SB_CION7383:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515135 SUNNYSD4 138 997799 SUNNYSD3 138 3 | 330 | 330 | 0.04417 | 103.63 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.34638 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.34638 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.34794 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.34831 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35092 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35092 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.38459 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 997799 SUNNYSD3 138 3 | 330 | 330 | 0.04417 | 102.54 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.27123 | 116.4 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 116.39 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 116.39 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 116.39 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.27989 | 109.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.33073 | 117.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.33073 | 117.5 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09381 | 112.08 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09411 | 112.07 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09411 | 112.07 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09526 | 112.07 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09526 | 112.07 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.09681 | 107.59 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.10964 | 111.98 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.27123 | 115.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 115.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 115.68 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.27207 | 115.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.27989 | 109.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.33073 | 117.6 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.33073 | 117.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03238 | 104.09 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03238 | 104.14 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03238 | 104.42 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03289 | 107.79 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03289 | 110.27 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03328 | 106.34 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03328 | 110.29 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03401 | 101.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03401 | 101.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03401 | 103.44 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03401 | 103.45 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03401 | 108.9 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05852 | 140.49 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05881 | 140.48 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05881 | 140.48 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05951 | 140.5 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05951 | 140.5 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06052 | 136.23 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06489 | 138.47 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03238 | 100.38 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03238 | 100.42 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03238 | 100.71 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03289 | 104.06 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03289 | 106.53 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03328 | 102.65 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03328 | 106.58 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03401 | 105.14 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05852 | 136.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05881 | 136.66 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05881 | 136.66 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05951 | 136.68 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05951 | 136.68 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06052 | 132.43 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06489 | 134.65 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.06929 | 103.05 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.06967 | 103.04 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.06967 | 103.04 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.0705 | 103.05 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.0705 | 103.05 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07662 | 101.15 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.06929 | 110.29 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.06967 | 110.27 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.06967 | 110.27 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.0705 | 110.28 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.0705 | 110.28 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07172 | 106.66 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07662 | 108.36 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04079 | 106.05 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05835 | 120.19 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05843 | 120.18 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05843 | 120.18 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05914 | 120.19 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05914 | 120.19 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06003 | 116.29 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06334 | 117.91 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04079 | 103.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05835 | 117.7 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05843 | 117.69 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05843 | 117.69 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05914 | 117.7 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05914 | 117.7 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.06003 | 113.81 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.06334 | 115.42 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.06929 | 117.94 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.06967 | 117.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.06967 | 117.93 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.0705 | 117.93 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.0705 | 117.93 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07172 | 114.28 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07662 | 116 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06929 | 116.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06967 | 116.1 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06967 | 116.1 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0705 | 116.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0705 | 116.1 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07172 | 112.46 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07662 | 114.17 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06929 | 116.1 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06967 | 116.09 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06967 | 116.09 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0705 | 116.09 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0705 | 116.09 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07172 | 112.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07662 | 114.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-168 | FROM->TO | 514868 DOUGLTP4 138 514922 CLASSEN4 138 1 | 268 | 287 | 0.37956 | 115.8 | 514861 MUSTANG4 138 514865 COUNCIL4 138 1 | TDF Impact | Multi - West Oaks - Council - Classen 138 kV Reconductor
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-169 | FROM->TO | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 187 | 211 | 0.94301 | 117.67 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-169 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 199 | 223 | 0.94153 | 116.8 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03082 | 109.27 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03082 | 109.27 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 531379 JONES3 115 531426 JAMESON3 115 1 | 119.5 | 148.2 | 0.07675 | 100.85 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 531379 JONES3 115 531448 HOLCOMB3 115 1 | 119.5 | 148.2 | 0.07675 | 106.84 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 355 | 355 | 0.05167 | 104.63 | Potential P4 Event - POI 531449_2 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.0317 | 115.93 | Potential P4 Event - POI 531449_2 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 531419 DOBSON 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.1719 | 115.14 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 531420 FLETCHR3 115 531440 WILLIAM3 115 1 | 99.6 | 99.6 | 0.05727 | 103.1 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 195.4 | 195.4 | 0.1719 | 131.7 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 531432 PILE 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.1719 | 114.1 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 195.4 | 195.4 | 0.11127 | 113.71 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-172 | FROM->TO | 531449 HOLCOMB7 345 997448 HOLCOMB 115 1 | 336 | 358.5 | 0.36672 | 100.35 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03082 | 109.27 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03082 | 109.27 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 531379 JONES3 115 531426 JAMESON3 115 1 | 119.5 | 148.2 | 0.07675 | 100.85 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 531379 JONES3 115 531448 HOLCOMB3 115 1 | 119.5 | 148.2 | 0.07675 | 106.84 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 355 | 355 | 0.05167 | 104.63 | Potential P4 Event - POI 531449_2 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.0317 | 115.93 | Potential P4 Event - POI 531449_2 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 531419 DOBSON 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.1719 | 115.14 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 531420 FLETCHR3 115 531440 WILLIAM3 115 1 | 99.6 | 99.6 | 0.05727 | 103.1 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 195.4 | 195.4 | 0.1719 | 131.7 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 531432 PILE 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.1719 | 114.1 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 195.4 | 195.4 | 0.11127 | 113.71 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-173 | FROM->TO | 531449 HOLCOMB7 345 997448 HOLCOMB 115 1 | 336 | 358.5 | 0.36672 | 100.35 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03149 | 111.68 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03302 | 113.49 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03302 | 113.55 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03483 | 108.6 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03485 | 108.5 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03486 | 109.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.2 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.24 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.26 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.32 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.33 | 548814 SUB M-161 161 775401 GEN-2023-171 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.33 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.34 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.35 | 52614 J2261 POI 500 338156 8POWERLN_RD% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.35 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.35 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.45 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.46 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.46 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.5 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.55 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.55 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.56 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.61 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.62 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.68 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.68 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.76 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.76 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.8 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.83 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.83 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.85 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 108.92 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 109 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 109.01 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 109.03 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 109.04 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 109.06 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 109.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 109.07 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 109.12 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 109.12 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 109.26 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03487 | 110.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03488 | 108.33 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03488 | 108.33 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03488 | 108.38 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03488 | 108.55 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03488 | 108.55 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03488 | 108.55 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03488 | 108.57 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03489 | 109.27 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03489 | 109.27 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0349 | 110.48 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03491 | 108.49 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03491 | 108.5 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03498 | 108.97 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.035 | 108.37 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03503 | 108.96 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03503 | 108.96 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03503 | 108.96 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03507 | 112.5 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03507 | 112.5 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03512 | 109.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03512 | 109.14 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03512 | 110.48 | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03513 | 109.06 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03516 | 109.26 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03531 | 109.26 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03586 | 111.14 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03586 | 111.15 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03651 | 112.42 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03702 | 114.43 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03737 | 116.18 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03737 | 116.26 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03737 | 116.26 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03737 | 116.26 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03749 | 116.46 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03828 | 119.05 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04599 | 112.32 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524648 CARGILL 3 115 524655 FRIONA 3 115 1 | 95.6 | 105 | 0.04368 | 122.86 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524648 CARGILL 3 115 524655 FRIONA 3 115 1 | 95.6 | 105 | 0.04368 | 123.27 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524648 CARGILL 3 115 524655 FRIONA 3 115 1 | 95.6 | 105 | 0.04563 | 111.52 | Potential P4 Event - POI 762216_14 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524648 CARGILL 3 115 524655 FRIONA 3 115 1 | 95.6 | 105 | 0.04563 | 111.52 | Potential P4 Event - POI 762467_7 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04368 | 162.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04368 | 162.53 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04449 | 133.15 | P12:115:SPS:T04_1_TRABLNC_CASTRO:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 151.08 | Potential P4 Event - POI 762216_14 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 151.08 | Potential P4 Event - POI 762467_7 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04565 | 131.46 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04566 | 133.77 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04566 | 133.81 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04566 | 133.81 | Potential P4 Event - POI 774180_0 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04566 | 133.81 | Potential P4 Event - POI 774180_1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04566 | 134.27 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04569 | 123.3 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04569 | 123.35 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.34 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.39 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.42 | P12:EHV:EES::8MCKNIGHT%:8FRANKLIN%:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.63 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.63 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.64 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.65 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.65 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.65 | P23:500:EES:PERVIL:R9872 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.65 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.66 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.66 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.66 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.68 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.68 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.69 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.69 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.69 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.69 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.7 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.7 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.7 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.7 | P13:SH902T GSU | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.71 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.71 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.71 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.72 | P11:024:DPC:ALMA2:6 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.72 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.72 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.73 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.73 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.73 | P13:GPPS#1 GSU-FUT | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.74 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.77 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.78 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.79 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.83 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.83 | P23:345:XEL:8H14 PRI | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.83 | P23:345:XEL:8H17 PRI AS | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.84 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.85 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.89 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.89 | P23:345:XEL:8N22 SHC | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.91 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.92 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.92 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.92 | P23:345:MEC:CBEC 908 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.93 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.94 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.94 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.97 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.97 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 121.97 | P23:345:MEC:CBEC 905 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 122 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 122.02 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 122.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 122.04 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 122.04 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 122.05 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 122.06 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 122.06 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 122.2 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 123.3 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 123.31 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 123.31 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 123.57 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 123.59 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 123.59 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 124.9 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 125.03 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 125.17 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 125.17 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 125.19 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 125.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04571 | 126.89 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04578 | 131.36 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04593 | 130.36 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04593 | 130.36 | Potential P4 Event - POI 525832_5 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04593 | 130.36 | Potential P4 Event - POI 525832_7 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524822 CURRY 3 115 524908 ROOSEVELT 3 115 2 | 158 | 174 | 0.06328 | 109.48 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 319 | 319 | 0.12443 | 103.99 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-178 | FROM->TO | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 319 | 319 | 0.12736 | 104.84 | 524770 PLSNT_HILL 6 230 524909 ROOSEVELT 6 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-180 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09651 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-180 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09651 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-180 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09651 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.20071 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.20071 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.20071 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06146 | 103.31 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06146 | 103.31 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06146 | 103.32 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06146 | 103.35 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06146 | 103.35 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06513 | 100.81 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06146 | 105.69 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06146 | 111.2 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06146 | 111.2 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06146 | 111.21 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06146 | 111.26 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06146 | 111.26 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06513 | 108.49 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03232 | 128.55 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03232 | 132.7 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03232 | 132.7 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03232 | 132.71 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03232 | 132.74 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03232 | 132.74 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03349 | 129.99 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06146 | 115.79 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06146 | 120.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06146 | 120.93 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06146 | 120.95 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06146 | 120.96 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06146 | 120.96 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06513 | 118.28 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03119 | 134.17 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 117.25 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 117.35 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 117.35 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 119.74 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 119.9 | Potential P4 Event - POI 764115_0 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 119.92 | Potential P4 Event - POI 764115_2 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 129.54 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04452 | 145.87 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03007 | 101.16 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03027 | 101.12 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0304 | 101.75 | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0304 | 102.06 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04135 | 125.8 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04135 | 125.8 | Potential P4 Event - POI 514801_4 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04135 | 125.81 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04135 | 125.87 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04135 | 125.87 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04335 | 125.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04797 | 113.55 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04797 | 113.9 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04797 | 113.9 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04797 | 116.2 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04797 | 117.7 | Potential P4 Event - POI 764115_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04797 | 117.71 | Potential P4 Event - POI 764115_2 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04797 | 126.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.06051 | 135.01 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03119 | 130.26 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 113.51 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 113.6 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 113.6 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 115.99 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 116.15 | Potential P4 Event - POI 764115_0 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 116.16 | Potential P4 Event - POI 764115_2 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0319 | 125.76 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04452 | 142.14 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03119 | 125.44 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0319 | 108.86 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0319 | 108.95 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0319 | 108.95 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0319 | 111.33 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0319 | 111.49 | Potential P4 Event - POI 764115_0 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0319 | 111.51 | Potential P4 Event - POI 764115_2 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0319 | 121.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04452 | 137.49 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.17686 | 105.43 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.17686 | 104.92 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03003 | 148.24 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03232 | 152.49 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03232 | 152.49 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03232 | 152.5 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03232 | 152.54 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03232 | 152.54 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03349 | 149.75 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04135 | 116.3 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04135 | 116.3 | Potential P4 Event - POI 514801_3 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04135 | 116.31 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04135 | 116.37 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04135 | 116.37 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04335 | 115.72 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04797 | 105.04 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04797 | 105.36 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04797 | 105.36 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04797 | 107.48 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04797 | 108.87 | Potential P4 Event - POI 764115_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04797 | 108.88 | Potential P4 Event - POI 764115_2 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04797 | 117.39 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06051 | 124.89 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06146 | 103.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06146 | 108.46 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06146 | 108.46 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06146 | 108.47 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06146 | 108.49 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06146 | 108.49 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06513 | 105.9 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33663 | 109.06 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33666 | 109.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33666 | 109.14 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33692 | 108.96 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33692 | 108.96 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33692 | 108.96 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33736 | 108.97 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33796 | 108.49 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33796 | 108.5 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33805 | 108.37 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3381 | 110.48 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33811 | 108.33 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33815 | 108.57 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33816 | 108.38 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33817 | 108.55 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33817 | 108.55 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33817 | 108.55 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33819 | 108.33 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3382 | 108.35 | 52614 J2261 POI 500 338156 8POWERLN_RD% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33828 | 108.24 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33828 | 108.35 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33828 | 108.45 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33828 | 108.83 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.2 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.26 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.32 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.33 | 548814 SUB M-161 161 775401 GEN-2023-171 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.33 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.34 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.35 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.46 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.46 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.5 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.55 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.55 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.56 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.61 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.62 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.68 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.68 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.76 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.76 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.8 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.83 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.85 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 108.92 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 109 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 109.01 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 109.03 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 109.04 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 109.06 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 109.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 109.07 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 109.12 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 109.12 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 109.26 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33829 | 110.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3383 | 109.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33872 | 108.6 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33878 | 108.5 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33879 | 109.27 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33879 | 109.27 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33988 | 110.48 | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34136 | 109.26 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34269 | 111.14 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34269 | 111.15 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34311 | 109.26 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34329 | 112.5 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34329 | 112.5 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34498 | 111.68 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34558 | 112.42 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34751 | 113.49 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34751 | 113.55 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35259 | 116.18 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35259 | 116.26 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35259 | 116.26 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35259 | 116.26 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35274 | 116.46 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35739 | 119.05 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.36097 | 112.32 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.36121 | 114.43 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50641 | 131.03 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50641 | 131.03 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50641 | 131.05 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50641 | 131.05 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50641 | 134.18 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50641 | 134.19 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50641 | 134.31 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50641 | 134.33 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50641 | 147.24 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.50641 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03295 | 100.15 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03295 | 100.34 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03295 | 100.34 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03295 | 100.86 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03295 | 100.86 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03295 | 101.61 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03295 | 101.61 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.43518 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.43518 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.43518 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.43518 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.43518 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.44075 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.45166 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.15654 | 109.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.15654 | 116.39 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.15654 | 116.39 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.15654 | 116.39 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.15654 | 116.4 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.18524 | 117.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.18524 | 117.5 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05772 | 107.59 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05772 | 112.07 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05772 | 112.07 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05772 | 112.07 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05772 | 112.07 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05772 | 112.08 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.06496 | 111.98 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.15654 | 109.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.15654 | 115.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.15654 | 115.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.15654 | 115.68 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.15654 | 115.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.18524 | 117.6 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.18524 | 117.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03915 | 136.23 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03915 | 140.48 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03915 | 140.48 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03915 | 140.49 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03915 | 140.5 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03915 | 140.5 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.04162 | 138.47 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03915 | 132.43 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03915 | 136.66 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03915 | 136.66 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03915 | 136.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03915 | 136.68 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03915 | 136.68 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04162 | 134.65 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05113 | 103.04 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05113 | 103.04 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05113 | 103.05 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05113 | 103.05 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05113 | 103.05 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.0539 | 101.15 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05113 | 106.66 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05113 | 110.27 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05113 | 110.27 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05113 | 110.28 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05113 | 110.28 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05113 | 110.29 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.0539 | 108.36 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04748 | 116.29 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04748 | 120.18 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04748 | 120.18 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04748 | 120.19 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04748 | 120.19 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04748 | 120.19 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04772 | 106.05 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04935 | 117.91 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04748 | 113.81 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04748 | 117.69 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04748 | 117.69 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04748 | 117.7 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04748 | 117.7 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04748 | 117.7 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04772 | 103.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04935 | 115.42 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05113 | 114.28 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05113 | 117.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05113 | 117.93 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05113 | 117.93 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05113 | 117.93 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05113 | 117.94 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.0539 | 116 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 112.46 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 116.1 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 116.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 116.1 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 116.1 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 116.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0539 | 114.17 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 112.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 116.09 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 116.09 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 116.09 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 116.09 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05113 | 116.1 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0539 | 114.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03071 | 124.79 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03118 | 117.45 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.0312 | 108.9 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.0312 | 110.77 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03202 | 113.18 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03202 | 113.18 | Potential P4 Event - POI 514801_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03202 | 113.23 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03317 | 120.41 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03317 | 120.45 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03317 | 120.45 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03317 | 120.45 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03317 | 120.65 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-188 | FROM->TO | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04452 | 101.18 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.12407 | 103.55 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.12407 | 108.1 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.12399 | 132.53 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 532937 NEOSHO 5 161 997363 NEOSHO TX-5 138 1 | 150 | 165 | 0.23237 | 110.57 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 532937 NEOSHO 5 161 997364 NEOSHO TX-4 138 1 | 112 | 123.2 | 0.17001 | 107.95 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 533020 NEOSHOS4 138 997363 NEOSHO TX-5 138 1 | 150 | 165 | 0.23237 | 110.35 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 533021 NEOSHO 4 138 997364 NEOSHO TX-4 138 1 | 112 | 123.2 | 0.17001 | 107.73 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 533758 CRAWFOR2 69.0 533772 SE1GREE2 69.0 1 | 48 | 57 | 0.04343 | 119.21 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 533762 GIR JCT2 69.0 533772 SE1GREE2 69.0 1 | 55 | 57 | 0.04343 | 112.47 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.54781 | 105.44 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8489 | 106.15 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8489 | 109.21 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8489 | 109.21 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85246 | 105.21 | P21:161:GRDA:MIAMI5-AFTON5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.42 | 655832 BLUEBUTE-MK7 115 655849 VEEDER -MK7 115 2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.45 | P12:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.46 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.46 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.47 | 516091 OKTAHA 7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.47 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.48 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.48 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.49 | P13:069-161:OPPD:S1217 T1:LT::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.5 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.5 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.54 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.54 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.55 | P12:345:XEL:ASAK-ECL SPS | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.56 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.57 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.58 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.6 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.61 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.65 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.71 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.75 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.81 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.87 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.88 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.9 | P11:230-22-18:EES:HOOKER_E | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 102.93 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.14 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.17 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.23 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.23 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.24 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.3 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.3 | P11:HV:EES::1ISES U1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.33 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.33 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.56 | 547479 LAR382 5 161 764315 GEN-2020-088 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.87 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.87 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 103.94 | P13:161-22:AEPW:FLINTCR5:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 104.26 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 104.59 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 104.59 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 105.67 | 547498 STL439 5 161 547655 S1G439 1 13.2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 105.74 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 105.74 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85257 | 105.74 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85258 | 102.51 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85258 | 102.55 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85258 | 102.55 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85258 | 102.69 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85258 | 102.74 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8526 | 102.72 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85263 | 103.83 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85265 | 102.97 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85265 | 107.04 | P21:161:GRDA:AFTON-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85269 | 104.57 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85271 | 102.85 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85273 | 105.05 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85274 | 103.38 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85274 | 103.53 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85275 | 105.33 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85275 | 105.33 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85275 | 105.72 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85277 | 104.15 | P12:HV:EES::5HILLTOP%:NORFORK5!:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85277 | 105.41 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85277 | 106.49 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85281 | 103.81 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85281 | 103.87 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85281 | 103.89 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85281 | 103.89 | P21:161:EES-EAI:ST_JOE_E:HILTOP_E:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85282 | 107.17 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85297 | 103.95 | P12:345:AEPW:ONETA--7:N.E.S.-7::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85308 | 105.37 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85313 | 104.17 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85326 | 104.07 | P12:138:WERE:LIBE-NSES-138:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8533 | 104.33 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85334 | 107.05 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8534 | 107.37 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8534 | 107.37 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.854 | 104.14 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85486 | 109.33 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85486 | 109.34 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85521 | 107.37 | Potential P4 Event - POI 770500_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85521 | 107.89 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85527 | 108.25 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85527 | 108.25 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85528 | 113.94 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85664 | 105.26 | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8569 | 119.66 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85716 | 107.94 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85729 | 104.66 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85929 | 113.64 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85929 | 113.64 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.86206 | 115.34 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-195 | FROM->TO | 524822 CURRY 3 115 524908 ROOSEVELT 3 115 2 | 158 | 174 | 0.0325 | 109.48 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-195 | FROM->TO | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 319 | 319 | 0.06388 | 103.99 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-195 | FROM->TO | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 319 | 319 | 0.06542 | 104.84 | 524770 PLSNT_HILL 6 230 524909 ROOSEVELT 6 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-199 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05491 | 106.25 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-199 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05491 | 106.25 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-199 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-199 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-205 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.18494 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-205 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.18494 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-205 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.18494 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-205 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.16313 | 101.6 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-205 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.16313 | 108 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-209 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03264 | 103.42 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-209 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03264 | 103.42 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-209 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03264 | 103.6 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-209 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 | 318.7 | 318.7 | 0.03077 | 104.57 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.04893 | 101.6 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.04893 | 108 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.07804 | 105.43 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.07804 | 104.92 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.20183 | 117.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.20183 | 117.5 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.21331 | 109.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.21331 | 116.39 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.21331 | 116.39 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.21331 | 116.39 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.21331 | 116.4 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.14482 | 111.98 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.14772 | 107.59 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.14772 | 112.07 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.14772 | 112.07 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.14772 | 112.07 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.14772 | 112.07 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.14772 | 112.08 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.20183 | 117.6 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.20183 | 117.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.21331 | 109.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.21331 | 115.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.21331 | 115.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.21331 | 115.68 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.21331 | 115.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03192 | 105.72 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03251 | 105.05 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03274 | 105.33 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03274 | 105.33 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.3775 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.3775 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.3775 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-212 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0355 | 109.26 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14286 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14286 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14286 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03515 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03703 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03703 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03703 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03703 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03703 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03703 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-216 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05174 | 106.25 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-216 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05174 | 106.25 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-216 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-216 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-217 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05174 | 106.25 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-217 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05174 | 106.25 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-217 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-217 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-218 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05174 | 106.25 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-218 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05174 | 106.25 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-218 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-218 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05647 | 106.25 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05647 | 106.25 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.26694 | 121.49 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.26807 | 122 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16137 | 130.45 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16917 | 137.35 | P12:230:SUNC:CONCORDIA-ELMCREEK::539639-539658(1):HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16917 | 137.35 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16946 | 125.29 | P12:115:HAST:::LINE 1159B EGYCNTR7 - SUTTON 7:HV:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17091 | 128.85 | P23:345:WERE:SUMM-345-218:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17102 | 128.07 | 539805 ELMCREEK7 345 3WXFMR ELMCREEK T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17102 | 128.08 | 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17102 | 128.11 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17102 | 130.55 | Potential P4 Event - POI 532773_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1716 | 129 | Potential P4 Event - POI 532773_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 123.49 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 123.57 | P12:345:XEL:ASAK-ECL SPS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 123.66 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 123.72 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 124.89 | P42:345:OKGE:SB_RARD7381:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 126.89 | Potential P4 Event - POI 515576_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.33 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.44 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.5 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.5 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.5 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.55 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.55 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.59 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.62 | 509745 CLARKSV7 345 760389 GEN-2017-140 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.68 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.7 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.75 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.75 | 508286 CAMPCOR4 138 765980 GEN-2021-075 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.78 | 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.78 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.81 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.81 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.92 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.96 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.96 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.02 | 525832 TUCO_INT 7 345 769921 GEN-2022-147 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.19 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.2 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.22 | 511477 S.W.S.-4 138 776561 GEN-2023-229 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.24 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.24 | P13:345:GRDA:GRDA2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.26 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.26 | P12:161:GRDA:SALINA 5-SALNCRK5:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.28 | 508298 LYDIA 7 345 764075 GEN-2020-054 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.35 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.41 | P11:230-22-18:EES:HOOKER_E | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.44 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.45 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.46 | P23:345:AEPW:NES CB 3413B NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.46 | P41:345:AEPW:NES CB 3413B NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.49 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.85 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.88 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.08 | 776401 GEN-2023-221 345 776402 G23-221XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.1 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.11 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.2 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.25 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.25 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.26 | 525481 PLANT_X 6 230 774821 GEN-2023-142 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.26 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.34 | P12:EHV:EES::8ANO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.47 | P11:25:EES:WATERF:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.47 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.48 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.5 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.54 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.68 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.68 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.78 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.78 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.01 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.15 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.16 | GEN-2023-102_POI_515852_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.36 | Potential P4 Event - POI 515576_20 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.59 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.59 | GEN-2021-005_POI_532773_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.84 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.88 | Potential P4 Event - POI 337561_27 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 127.62 | 640218 HEBRN N7 115 640012 HEBRON G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 128.13 | Potential P4 Event - POI 515852_14 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 129.11 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17179 | 123.37 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17179 | 129.49 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1718 | 123.59 | P23:345:MEC:HILLS:934::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1718 | 124.82 | P42:500:OKGE:SB_FTTH8581:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1718 | 124.85 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17182 | 123.89 | 635580 ARBOR HILL 3 345 635622 RCCN TRL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17217 | 124.75 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17217 | 124.75 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17217 | 124.75 | P45:345:OPPD:S3454-S3455&WAG:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17232 | 124.13 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19841 | 136.47 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19841 | 138.29 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23453 | 164.92 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23453 | 165.19 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26718 | 187.53 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31037 | 154.46 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31037 | 154.52 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31376 | 153.19 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31376 | 153.2 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31378 | 152.6 | P23:345:GMO-AECI:STJOE-R3-14:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31378 | 153.17 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31379 | 153.22 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31383 | 152.3 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31384 | 152.59 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31384 | 152.59 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31385 | 152.55 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.01 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.04 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.04 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.31 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.46 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.59 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.61 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.83 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 153.98 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.76 | 300014 1HOLDNG13 13.8 301561 5HOLDENB1 161 13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.76 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.77 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.77 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.99 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.03 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.03 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.05 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.05 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.05 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.05 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.07 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.07 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.09 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.09 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.1 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.11 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.15 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.2 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.21 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.21 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.21 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.21 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.21 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.26 | 764795 GEN-2020-094 345 764805 G20-094-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.28 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.29 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.33 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.4 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.4 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.47 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.49 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.49 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.52 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.57 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.65 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.65 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.66 | P13:GPPS#1 GSU-FUT | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.78 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.8 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.8 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.91 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.93 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.13 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.17 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.48 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.77 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.79 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.89 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.89 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 154.01 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 154.08 | Potential P4 Event - POI 640588_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 154.24 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 155.08 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 155.71 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 158.34 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31389 | 152.16 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31392 | 152.09 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31392 | 152.37 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31393 | 152.05 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31393 | 152.2 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31393 | 152.2 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31402 | 153.96 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31447 | 153.71 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31447 | 153.77 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31447 | 154.51 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31489 | 153.21 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31761 | 153.25 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31761 | 153.38 | P12:115:WERE:KNOB-MARS-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32163 | 154.45 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32974 | 157.17 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34168 | 167.12 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34168 | 167.42 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34965 | 164.67 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37506 | 182.47 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55818 | 269.01 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40117 | 144.39 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40117 | 144.45 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40555 | 143.19 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40555 | 143.2 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40557 | 142.62 | P23:345:GMO-AECI:STJOE-R3-14:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40557 | 143.17 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40559 | 143.22 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40564 | 142.33 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40566 | 142.61 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40566 | 142.61 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40568 | 142.58 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40569 | 142.63 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40569 | 142.84 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40569 | 143.94 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.08 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.08 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.09 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.09 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.09 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.09 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.14 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.16 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.25 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.25 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.25 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.34 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.49 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.61 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 141.09 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 141.82 | 300014 1HOLDNG13 13.8 301561 5HOLDENB1 161 13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 141.82 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 141.82 | 520882 DOVERSW4 138 762493 GEN-2018-011 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.04 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.08 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.11 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.12 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.14 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.14 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.2 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.24 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.25 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.25 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.3 | 764795 GEN-2020-094 345 764805 G20-094-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.31 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.33 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.36 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.43 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.43 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.5 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.52 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.52 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.55 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.59 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.67 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.67 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.68 | P13:GPPS#1 GSU-FUT | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.8 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.81 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.81 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.92 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.94 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.12 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.17 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.2 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.47 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.56 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.74 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.76 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.84 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.85 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 144.03 | Potential P4 Event - POI 640588_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 144.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 144.99 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 145.61 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 148.12 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40572 | 142.2 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40576 | 142.14 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40576 | 142.41 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40577 | 142.1 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40577 | 142.24 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40578 | 142.24 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40589 | 143.92 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40647 | 143.69 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40647 | 143.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40647 | 144.45 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40701 | 143.21 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41053 | 143.25 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41053 | 143.37 | P12:115:WERE:KNOB-MARS-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41572 | 144.4 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42621 | 147 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45194 | 154.18 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48479 | 171.22 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61341 | 211.32 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61341 | 214.43 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61341 | 214.67 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 2 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31037 | 151.15 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31037 | 151.21 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31376 | 149.88 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31376 | 149.89 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31378 | 149.28 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31378 | 149.86 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31379 | 149.91 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31383 | 148.95 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31384 | 149.26 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31384 | 149.26 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31385 | 149.23 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 148.68 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 148.7 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 148.7 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 148.98 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 149.13 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 149.27 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 149.28 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 149.51 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 150.67 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.42 | 300014 1HOLDNG13 13.8 301561 5HOLDENB1 161 13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.42 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.44 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.66 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.69 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.7 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.71 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.71 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.71 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.71 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.74 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.74 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.76 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.76 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.77 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.78 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.82 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.87 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.88 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.88 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.88 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.88 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.88 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.93 | 764795 GEN-2020-094 345 764805 G20-094-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.95 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.97 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.07 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.07 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.14 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.17 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.17 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.2 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.24 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.33 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.33 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.34 | P13:GPPS#1 GSU-FUT | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.46 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.48 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.48 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.59 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.62 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.81 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.86 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.9 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.9 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.91 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.46 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.57 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.7 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.78 | Potential P4 Event - POI 640588_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.93 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 151.8 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 152.48 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 155.14 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31389 | 148.83 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31392 | 148.77 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31392 | 149.05 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31393 | 148.72 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31393 | 148.87 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31393 | 148.87 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31402 | 150.65 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31447 | 150.42 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31447 | 150.47 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31447 | 151.22 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31489 | 149.91 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31761 | 149.94 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31761 | 150.07 | P12:115:WERE:KNOB-MARS-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32163 | 151.17 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32974 | 153.94 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34168 | 164.09 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34168 | 164.39 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34965 | 161.59 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37506 | 179.75 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55818 | 268.09 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13558 | 103.48 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13558 | 103.52 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.15464 | 116.6 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 2 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05647 | 106.25 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05647 | 106.25 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.26694 | 121.49 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.26807 | 122 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16137 | 130.45 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16917 | 137.35 | P12:230:SUNC:CONCORDIA-ELMCREEK::539639-539658(1):HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16917 | 137.35 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16946 | 125.29 | P12:115:HAST:::LINE 1159B EGYCNTR7 - SUTTON 7:HV:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17091 | 128.85 | P23:345:WERE:SUMM-345-218:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17102 | 128.07 | 539805 ELMCREEK7 345 3WXFMR ELMCREEK T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17102 | 128.08 | 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17102 | 128.11 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17102 | 130.55 | Potential P4 Event - POI 532773_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1716 | 129 | Potential P4 Event - POI 532773_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 123.49 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 123.57 | P12:345:XEL:ASAK-ECL SPS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 123.66 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 123.72 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 124.89 | P42:345:OKGE:SB_RARD7381:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17177 | 126.89 | Potential P4 Event - POI 515576_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.33 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.44 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.5 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.5 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.5 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.55 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.55 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.59 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.62 | 509745 CLARKSV7 345 760389 GEN-2017-140 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.68 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.7 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.75 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.75 | 508286 CAMPCOR4 138 765980 GEN-2021-075 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.78 | 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.78 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.81 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.81 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.92 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.96 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 123.96 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.02 | 525832 TUCO_INT 7 345 769921 GEN-2022-147 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.19 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.2 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.22 | 511477 S.W.S.-4 138 776561 GEN-2023-229 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.24 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.24 | P13:345:GRDA:GRDA2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.26 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.26 | P12:161:GRDA:SALINA 5-SALNCRK5:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.28 | 508298 LYDIA 7 345 764075 GEN-2020-054 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.35 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.41 | P11:230-22-18:EES:HOOKER_E | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.44 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.45 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.46 | P23:345:AEPW:NES CB 3413B NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.46 | P41:345:AEPW:NES CB 3413B NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.49 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.85 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 124.88 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.08 | 776401 GEN-2023-221 345 776402 G23-221XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.1 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.11 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.2 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.25 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.25 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.26 | 525481 PLANT_X 6 230 774821 GEN-2023-142 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.26 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.34 | P12:EHV:EES::8ANO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.47 | P11:25:EES:WATERF:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.47 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.48 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.5 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.54 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.68 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.68 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.78 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 125.78 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.01 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.15 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.16 | GEN-2023-102_POI_515852_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.36 | Potential P4 Event - POI 515576_20 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.59 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.59 | GEN-2021-005_POI_532773_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.84 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 126.88 | Potential P4 Event - POI 337561_27 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 127.62 | 640218 HEBRN N7 115 640012 HEBRON G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 128.13 | Potential P4 Event - POI 515852_14 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17178 | 129.11 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17179 | 123.37 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17179 | 129.49 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1718 | 123.59 | P23:345:MEC:HILLS:934::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1718 | 124.82 | P42:500:OKGE:SB_FTTH8581:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1718 | 124.85 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17182 | 123.89 | 635580 ARBOR HILL 3 345 635622 RCCN TRL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17217 | 124.75 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17217 | 124.75 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17217 | 124.75 | P45:345:OPPD:S3454-S3455&WAG:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17232 | 124.13 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19841 | 136.47 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19841 | 138.29 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23453 | 164.92 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23453 | 165.19 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26718 | 187.53 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31037 | 154.46 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31037 | 154.52 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31376 | 153.19 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31376 | 153.2 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31378 | 152.6 | P23:345:GMO-AECI:STJOE-R3-14:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31378 | 153.17 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31379 | 153.22 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31383 | 152.3 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31384 | 152.59 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31384 | 152.59 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31385 | 152.55 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.01 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.04 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.04 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.31 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.46 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.59 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.61 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 152.83 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31387 | 153.98 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.76 | 300014 1HOLDNG13 13.8 301561 5HOLDENB1 161 13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.76 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.77 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.77 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 151.99 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.03 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.03 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.05 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.05 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.05 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.05 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.07 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.07 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.09 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.09 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.1 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.11 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.15 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.2 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.21 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.21 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.21 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.21 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.21 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.26 | 764795 GEN-2020-094 345 764805 G20-094-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.28 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.29 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.33 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.4 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.4 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.47 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.49 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.49 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.52 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.57 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.65 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.65 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.66 | P13:GPPS#1 GSU-FUT | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.78 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.8 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.8 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.91 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 152.93 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.13 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.17 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.48 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.77 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.79 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.89 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 153.89 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 154.01 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 154.08 | Potential P4 Event - POI 640588_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 154.24 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 155.08 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 155.71 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31388 | 158.34 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31389 | 152.16 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31392 | 152.09 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31392 | 152.37 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31393 | 152.05 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31393 | 152.2 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31393 | 152.2 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31402 | 153.96 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31447 | 153.71 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31447 | 153.77 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31447 | 154.51 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31489 | 153.21 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31761 | 153.25 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31761 | 153.38 | P12:115:WERE:KNOB-MARS-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32163 | 154.45 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32974 | 157.17 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34168 | 167.12 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34168 | 167.42 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34965 | 164.67 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37506 | 182.47 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55818 | 269.01 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40117 | 144.39 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40117 | 144.45 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40555 | 143.19 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40555 | 143.2 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40557 | 142.62 | P23:345:GMO-AECI:STJOE-R3-14:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40557 | 143.17 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40559 | 143.22 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40564 | 142.33 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40566 | 142.61 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40566 | 142.61 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40568 | 142.58 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40569 | 142.63 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40569 | 142.84 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40569 | 143.94 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.08 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.08 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.09 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.09 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.09 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.09 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.14 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.16 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.25 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.25 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.25 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.34 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.49 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4057 | 142.61 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 141.09 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 141.82 | 300014 1HOLDNG13 13.8 301561 5HOLDENB1 161 13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 141.82 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 141.82 | 520882 DOVERSW4 138 762493 GEN-2018-011 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.04 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.08 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.11 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.12 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.14 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.14 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.2 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.24 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.25 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.25 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.3 | 764795 GEN-2020-094 345 764805 G20-094-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.31 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.33 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.36 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.43 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.43 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.5 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.52 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.52 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.55 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.59 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.67 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.67 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.68 | P13:GPPS#1 GSU-FUT | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.8 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.81 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.81 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.92 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 142.94 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.12 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.17 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.2 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.47 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.56 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.74 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.76 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.84 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.85 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 143.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 144.03 | Potential P4 Event - POI 640588_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 144.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 144.99 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 145.61 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40571 | 148.12 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40572 | 142.2 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40576 | 142.14 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40576 | 142.41 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40577 | 142.1 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40577 | 142.24 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40578 | 142.24 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40589 | 143.92 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40647 | 143.69 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40647 | 143.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40647 | 144.45 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40701 | 143.21 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41053 | 143.25 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41053 | 143.37 | P12:115:WERE:KNOB-MARS-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41572 | 144.4 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42621 | 147 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45194 | 154.18 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48479 | 171.22 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61341 | 211.32 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61341 | 214.43 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61341 | 214.67 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31037 | 151.15 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31037 | 151.21 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31376 | 149.88 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31376 | 149.89 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31378 | 149.28 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31378 | 149.86 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31379 | 149.91 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31383 | 148.95 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31384 | 149.26 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31384 | 149.26 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31385 | 149.23 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 148.68 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 148.7 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 148.7 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 148.98 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 149.13 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 149.27 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 149.28 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 149.51 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31387 | 150.67 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.42 | 300014 1HOLDNG13 13.8 301561 5HOLDENB1 161 13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.42 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.44 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.66 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.69 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.7 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.71 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.71 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.71 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.71 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.74 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.74 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.76 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.76 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.77 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.78 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.82 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.87 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.88 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.88 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.88 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.88 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.88 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.93 | 764795 GEN-2020-094 345 764805 G20-094-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.95 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 148.97 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.07 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.07 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.14 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.17 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.17 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.2 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.24 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.33 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.33 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.34 | P13:GPPS#1 GSU-FUT | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.46 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.48 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.48 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.59 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.62 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.81 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.86 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.9 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.9 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 149.91 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.46 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.57 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.7 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.78 | Potential P4 Event - POI 640588_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 150.93 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 151.8 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 152.48 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31388 | 155.14 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31389 | 148.83 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31392 | 148.77 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31392 | 149.05 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31393 | 148.72 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31393 | 148.87 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31393 | 148.87 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31402 | 150.65 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31447 | 150.42 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31447 | 150.47 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31447 | 151.22 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31489 | 149.91 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31761 | 149.94 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31761 | 150.07 | P12:115:WERE:KNOB-MARS-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32163 | 151.17 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32974 | 153.94 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34168 | 164.09 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34168 | 164.39 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34965 | 161.59 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37506 | 179.75 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55818 | 268.09 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13558 | 103.48 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13558 | 103.52 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.15464 | 116.6 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.07756 | 105.43 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.07756 | 104.92 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09889 | 119.05 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09911 | 116.46 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0997 | 112.42 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10902 | 116.18 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10902 | 116.26 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10902 | 116.26 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10902 | 116.26 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11017 | 111.14 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11017 | 111.15 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1122 | 110.48 | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11524 | 112.5 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11524 | 112.5 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1173 | 109.27 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1173 | 109.27 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11779 | 108.5 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11789 | 108.6 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11805 | 109.06 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11805 | 109.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11805 | 109.14 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11809 | 109.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.2 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.24 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.26 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.32 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.33 | 548814 SUB M-161 161 775401 GEN-2023-171 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.33 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.34 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.35 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.35 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.45 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.46 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.46 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.5 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.55 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.55 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.56 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.61 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.62 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.68 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.68 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.76 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.76 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.8 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.83 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.83 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.85 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 108.92 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 109 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 109.01 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 109.03 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 109.04 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 109.06 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 109.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 109.07 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 109.12 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 109.12 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 109.26 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1181 | 110.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11811 | 108.35 | 52614 J2261 POI 500 338156 8POWERLN_RD% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11812 | 108.33 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11812 | 108.33 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11812 | 108.38 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11812 | 108.55 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11812 | 108.55 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11812 | 108.55 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11812 | 108.57 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11812 | 110.48 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11813 | 108.49 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11813 | 108.5 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11816 | 108.37 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11816 | 108.97 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11818 | 108.96 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11818 | 108.96 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11818 | 108.96 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11824 | 109.26 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11832 | 109.26 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11957 | 111.68 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.12063 | 113.49 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.12063 | 113.55 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.12363 | 112.32 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.12437 | 114.43 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15315 | 131.03 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15315 | 131.03 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15315 | 131.05 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15315 | 131.05 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15315 | 134.18 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15315 | 134.19 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15315 | 134.31 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15315 | 134.33 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15315 | 147.24 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.15315 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10641 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10641 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10641 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10641 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10641 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10967 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.12339 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.05099 | 109.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.05099 | 116.39 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.05099 | 116.39 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.05099 | 116.39 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.05099 | 116.4 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.08054 | 117.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 478 | 478 | 0.08054 | 117.5 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.05099 | 109.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.05099 | 115.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.05099 | 115.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.05099 | 115.68 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.05099 | 115.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.08054 | 117.6 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 478 | 478 | 0.08054 | 117.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.19587 | 105.11 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.19587 | 105.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.19587 | 105.11 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11034 | 103.31 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11034 | 103.31 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11034 | 103.32 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11034 | 103.35 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11034 | 103.35 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11224 | 100.81 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11034 | 105.69 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11034 | 111.2 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11034 | 111.2 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11034 | 111.21 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11034 | 111.26 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11034 | 111.26 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11224 | 108.49 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09415 | 103.98 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09773 | 107.22 | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09773 | 108.31 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10119 | 128.55 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10119 | 132.7 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10119 | 132.7 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10119 | 132.71 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10119 | 132.74 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10119 | 132.74 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1018 | 129.99 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1119 | 109.45 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1119 | 111.27 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1119 | 112.45 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11034 | 115.79 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11034 | 120.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11034 | 120.93 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11034 | 120.95 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11034 | 120.96 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11034 | 120.96 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11224 | 118.28 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08379 | 111.45 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08443 | 107.98 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0857 | 115.96 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08716 | 102.3 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08716 | 102.33 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08716 | 102.33 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08727 | 101.74 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08728 | 101.73 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.48 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.49 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.74 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.74 | P13:230:EES:NINEMI:AT5 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.74 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.75 | 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.75 | 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.76 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.76 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.77 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.77 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.77 | P11:230-22-18:EES:HOOKER_E | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.79 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.81 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.85 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.85 | P11:HV:EES::1ISES U1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.86 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.86 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.87 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.87 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.88 | P11:25:EES:WATERF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.88 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 101.89 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 102.18 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 102.2 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 102.38 | 775520 G23-177-TAP 138 775521 GEN-2023-177 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 102.59 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 102.6 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 102.6 | GEN-2022-238_POI_515055_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 102.86 | 774660 G23-134-TAP 138 774661 GEN-2023-134 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 102.86 | 774661 GEN-2023-134 138 774662 G23-134XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08729 | 102.86 | GEN-2023-134_POI_774660_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0873 | 101.75 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0873 | 101.98 | P23:345:AEPW:NES CB 3417B NBTB:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0873 | 101.98 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08731 | 101.73 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08731 | 101.84 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08731 | 101.87 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08731 | 102.17 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08732 | 101.87 | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08733 | 101.97 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08733 | 101.97 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08733 | 102.22 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08734 | 101.85 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08734 | 102.19 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08735 | 101.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0874 | 102.62 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08742 | 102.92 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08752 | 103.5 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08752 | 104.41 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08783 | 103.24 | P12:138:OKGE:BKRBKR95:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08798 | 103.27 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09117 | 108.79 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09415 | 114.46 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09415 | 114.46 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09415 | 116.93 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09415 | 116.95 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09415 | 123.39 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09773 | 126.17 | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09773 | 127.26 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10119 | 152.49 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10119 | 152.49 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10119 | 152.5 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10119 | 152.54 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10119 | 152.54 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1018 | 149.75 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.10441 | 148.24 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1119 | 128.49 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1119 | 130.42 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1119 | 131.64 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11034 | 103.4 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11034 | 108.46 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11034 | 108.46 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11034 | 108.47 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11034 | 108.49 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11034 | 108.49 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11224 | 105.9 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.26902 | 112.5 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.26902 | 112.5 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27352 | 109.06 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27355 | 109.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27355 | 109.14 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27386 | 108.96 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27386 | 108.96 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27386 | 108.96 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27431 | 108.97 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27492 | 108.49 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27492 | 108.5 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27499 | 108.37 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27506 | 110.48 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27507 | 108.33 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27512 | 108.57 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27513 | 108.38 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27514 | 108.55 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27514 | 108.55 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27514 | 108.55 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27516 | 108.33 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27517 | 108.35 | 52614 J2261 POI 500 338156 8POWERLN_RD% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.2 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.24 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.26 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.32 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.33 | 548814 SUB M-161 161 775401 GEN-2023-171 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.33 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.34 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.35 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.35 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.45 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.46 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.46 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.5 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.55 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.55 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.56 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.61 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.62 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.68 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.68 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.76 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.76 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.8 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.83 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.83 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.85 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 108.92 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 109 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 109.01 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 109.03 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 109.04 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 109.06 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 109.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 109.07 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 109.12 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 109.12 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 109.26 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27525 | 110.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27526 | 109.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27559 | 109.27 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27559 | 109.27 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27565 | 108.6 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27569 | 108.5 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27575 | 110.48 | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27797 | 111.14 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27797 | 111.15 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27826 | 109.26 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27998 | 109.26 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28003 | 112.42 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28111 | 116.18 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28111 | 116.26 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28111 | 116.26 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28111 | 116.26 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28198 | 116.46 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28366 | 119.05 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28865 | 114.43 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.2915 | 112.32 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.29259 | 111.68 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.29928 | 113.49 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.29928 | 113.55 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38905 | 131.03 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38905 | 131.03 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38905 | 131.05 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38905 | 131.05 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38905 | 134.18 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38905 | 134.19 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38905 | 134.31 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38905 | 134.33 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38905 | 147.24 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.38905 | 108.02 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03681 | 104.86 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03681 | 106.26 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03681 | 109.17 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03409 | 100.6 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03409 | 102.09 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03409 | 103.17 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03209 | 100.12 | P42:345:OKGE:SB_CION7383:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03331 | 100.15 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03331 | 100.34 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03331 | 100.34 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03331 | 100.86 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03331 | 100.86 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03331 | 101.61 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03331 | 101.61 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03409 | 111.19 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03409 | 112.68 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03409 | 113.76 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.30707 | 107.81 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.30981 | 110.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.30981 | 110.11 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.30981 | 110.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.30981 | 110.18 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.30981 | 110.18 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.31832 | 109.24 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05265 | 101.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05265 | 101.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05265 | 103.44 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05265 | 103.45 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05265 | 108.9 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05468 | 104.09 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05468 | 104.14 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05468 | 104.42 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06246 | 136.23 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06246 | 140.48 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06246 | 140.48 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06246 | 140.49 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06246 | 140.5 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06246 | 140.5 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06373 | 138.47 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06537 | 107.79 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06537 | 110.27 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06691 | 106.34 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06691 | 110.29 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05265 | 105.14 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05468 | 100.38 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05468 | 100.42 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05468 | 100.71 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06246 | 132.43 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06246 | 136.66 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06246 | 136.66 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06246 | 136.68 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06246 | 136.68 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06246 | 136.68 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06373 | 134.65 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06537 | 104.06 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06537 | 106.53 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06691 | 102.65 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06691 | 106.58 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08789 | 103.04 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08789 | 103.04 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08789 | 103.05 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08789 | 103.05 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08789 | 103.05 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08932 | 101.15 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08789 | 106.66 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08789 | 110.27 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08789 | 110.27 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08789 | 110.28 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08789 | 110.28 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08789 | 110.29 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08932 | 108.36 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08632 | 106.05 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08886 | 116.29 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08886 | 120.18 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08886 | 120.18 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08886 | 120.19 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08886 | 120.19 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08886 | 120.19 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08982 | 117.91 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08632 | 103.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08886 | 113.81 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08886 | 117.69 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08886 | 117.69 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08886 | 117.7 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08886 | 117.7 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08886 | 117.7 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08982 | 115.42 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08789 | 114.28 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08789 | 117.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08789 | 117.93 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08789 | 117.93 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08789 | 117.93 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08789 | 117.94 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08932 | 116 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 112.46 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 116.1 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 116.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 116.1 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 116.1 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 116.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08932 | 114.17 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 112.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 116.09 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 116.09 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 116.09 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 116.09 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08789 | 116.1 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08932 | 114.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0332 | 247.85 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 209.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | Potential P4 Event - POI 525832_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04271 | 225.08 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04271 | 225.08 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04304 | 212.09 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.1 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.65 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.66 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.66 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.79 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04378 | 201.78 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0438 | 201.46 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04381 | 206.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04382 | 201.9 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04382 | 204.27 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04384 | 199.42 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04384 | 199.51 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 198.86 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:IPSCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.1 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.11 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.11 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.14 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.15 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | P12:EHV:EES::8SANS SOUCI%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.19 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EAI:NBF_SAN SO~1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.22 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.22 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.23 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.24 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.29 | P13:SH902T GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.3 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.34 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.35 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.36 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.41 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.44 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.46 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.51 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.53 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.53 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.63 | P23:345:XEL:8N8 MNN | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.64 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.67 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.73 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.74 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.8 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.86 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.86 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.89 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.91 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.92 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.06 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.09 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.09 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 201.31 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 201.31 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.07 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.08 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.08 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04412 | 210.59 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04582 | 209.74 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04927 | 232.94 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.05294 | 223.01 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03235 | 117.95 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.92 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03253 | 116.31 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 115.92 | Potential P4 Event - POI 776000_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 118.16 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03264 | 113.65 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03268 | 115.04 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03285 | 114.66 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 115.18 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 115.18 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.19 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.2 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.2 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.21 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.83 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.88 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.7 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.1 | ASGI-2021-003_POI_766051_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.25 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.4 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.4 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.62 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.62 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.67 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.67 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.69 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.69 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.7 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.73 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.73 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.97 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.97 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 113.18 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 113.18 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03357 | 116.56 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.04206 | 163.59 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03235 | 117.35 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03253 | 115.55 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 115.26 | Potential P4 Event - POI 773600_9 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 117.52 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03264 | 112.96 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03268 | 114.35 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03285 | 113.94 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 114.44 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 114.45 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.51 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.52 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.52 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.54 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.15 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.03 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.32 | ASGI-2021-003_POI_766051_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.49 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.63 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.65 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.88 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.88 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.89 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.89 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.9 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.91 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.91 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.93 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.93 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.94 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.94 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.98 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.02 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.02 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.27 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.27 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.45 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.45 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03357 | 115.94 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.04206 | 164.59 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.11154 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.11154 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.11154 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.12545 | 102.19 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.12545 | 101.74 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.25573 | 112.3 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.25573 | 112.3 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 103.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 103.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 110.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 110.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 110.6 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 110.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.25573 | 112.61 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.25573 | 112.61 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 103.44 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 103.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 110.17 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 110.17 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 110.17 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26254 | 110.18 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531379 JONES3 115 531426 JAMESON3 115 1 | 119.5 | 148.2 | 0.05335 | 100.26 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531379 JONES3 115 531448 HOLCOMB3 115 1 | 119.5 | 148.2 | 0.05335 | 106.23 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 355 | 355 | 0.1432 | 103.01 | Potential P4 Event - POI 531449_2 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07227 | 105.37 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07227 | 105.37 | Potential P4 Event - POI 531449_1 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07388 | 102.06 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07415 | 101.84 | Potential P4 Event - POI 523853_0 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07415 | 106.16 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.07415 | 113.68 | Potential P4 Event - POI 531449_2 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531419 DOBSON 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.12984 | 112.38 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531420 FLETCHR3 115 531440 WILLIAM3 115 1 | 99.6 | 99.6 | 0.04146 | 101.17 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 211.7 | 229 | 0.12984 | 109.63 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531432 PILE 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.12984 | 111.35 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 195.4 | 195.4 | 0.07649 | 113.12 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-015 | FROM->TO | 531449 HOLCOMB7 345 997448 HOLCOMB 115 1 | 336 | 358.5 | 0.27049 | 100.11 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-027 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.16394 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-027 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.16394 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-027 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.16394 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0418 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0439 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04393 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04393 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04393 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04393 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04393 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-027 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04393 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-028 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.47 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.10557 | 100.9 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.10557 | 105.66 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 110.37 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 111.83 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-028 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.03364 | 105.21 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-033 | FROM->TO | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 187 | 211 | 0.88086 | 118.87 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-033 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.03055 | 102.17 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-033 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 199 | 223 | 0.94228 | 116.33 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05111 | 127.1 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.7 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.82 | 560088 G16-063-TAP 345 768941 GEN-2022-098 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.83 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.83 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.83 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.83 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.84 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.84 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.85 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.86 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.87 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.87 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.87 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.87 | P23:345:XEL:8N17 SHC | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 110.87 | P23:345:XEL:8N22 SHC | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.11 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.12 | 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.12 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.12 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.13 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.17 | 505522 VAN BUR5 161 773101 GEN-2023-056 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.18 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.18 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.19 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.19 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.19 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.19 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.21 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.21 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.22 | P13:230:EES:NINEMI:AT4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.23 | P13:230:EES:NINEMI:AT5 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.28 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.3 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.31 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.31 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.32 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.32 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.32 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.32 | P11:HV:EES::1ISES U1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.36 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.38 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.45 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.46 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.46 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.5 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.51 | P11:25:EES:WATERF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.51 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.51 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.62 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.66 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.66 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.67 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.8 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.84 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.89 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.93 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 111.93 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 112.15 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 112.21 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 112.52 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 112.63 | 776181 GEN-2023-210 138 776182 G23-210XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 113.01 | 775520 G23-177-TAP 138 775521 GEN-2023-177 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 113.01 | GEN-2023-177_POI_775520_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 113.55 | 766110 GEN-2021-088 138 766111 G21-088-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 113.55 | 766114 G21-088-XFM1 34.5 766110 GEN-2021-088 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05137 | 113.55 | GEN-2021-088_POI_766111_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05138 | 112.56 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05138 | 113.57 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.0514 | 113.99 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.0514 | 114.87 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.0514 | 124.79 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.0514 | 125.31 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.0514 | 125.64 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05144 | 113.21 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05156 | 125.01 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05156 | 125.39 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05156 | 125.39 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05156 | 127.24 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05156 | 128.75 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05156 | 128.76 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05156 | 136.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05162 | 157.46 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05162 | 157.46 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05162 | 161.87 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05162 | 161.87 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05162 | 161.88 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05162 | 161.91 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05162 | 161.91 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05168 | 159.44 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.16008 | 141.09 | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05111 | 126.77 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.36 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.48 | 560088 G16-063-TAP 345 768941 GEN-2022-098 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.49 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.49 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.49 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.49 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.51 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.51 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.51 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.52 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.53 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.53 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.53 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.53 | P23:345:XEL:8N17 SHC | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.53 | P23:345:XEL:8N22 SHC | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.77 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.78 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.78 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.79 | 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.8 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.83 | 505522 VAN BUR5 161 773101 GEN-2023-056 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.84 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.84 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.85 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.85 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.85 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.85 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.87 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.87 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.88 | P13:230:EES:NINEMI:AT4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.89 | P13:230:EES:NINEMI:AT5 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.95 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.96 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.98 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.98 | P11:HV:EES::1ISES U1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.98 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.98 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.99 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 110.99 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.03 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.04 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.11 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.16 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.17 | P11:25:EES:WATERF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.17 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.17 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.28 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.32 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.33 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.34 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.47 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.5 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.56 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.59 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.59 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.81 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 111.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 112.18 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 112.3 | 776181 GEN-2023-210 138 776182 G23-210XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 112.67 | 775520 G23-177-TAP 138 775521 GEN-2023-177 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 112.67 | GEN-2023-177_POI_775520_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 113.22 | 766110 GEN-2021-088 138 766111 G21-088-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 113.22 | 766114 G21-088-XFM1 34.5 766110 GEN-2021-088 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05137 | 113.22 | GEN-2021-088_POI_766111_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05138 | 112.22 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05138 | 113.24 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.0514 | 113.65 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.0514 | 114.54 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.0514 | 124.47 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.0514 | 124.99 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.0514 | 125.32 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05144 | 112.88 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05156 | 124.69 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05156 | 125.07 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05156 | 125.07 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05156 | 126.92 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05156 | 128.43 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05156 | 128.44 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05156 | 135.95 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05162 | 157.18 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05162 | 157.18 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05162 | 161.59 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05162 | 161.59 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05162 | 161.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05162 | 161.63 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05162 | 161.63 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05168 | 159.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.16008 | 140.73 | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 278.75 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 278.75 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 278.78 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 278.81 | Potential P4 Event - POI 764115_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 278.81 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 278.87 | 521089 WASHITA4 138 3WXFMR WASHITA 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 278.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.1 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.1 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.15 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.15 | 520828 BLANCHD2 69.0 521018 OU SW 2 69.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.15 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.2 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.2 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.2 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.2 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 279.23 | P11:069:WFEC:ANADRK3:42MW::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 281.92 | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 287.46 | 520508 CLVJCTN2 69.0 520859 COGAR 2 69.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 287.46 | P12:138:WFEC:CLVLND_SCOTT:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03275 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03275 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03275 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.03192 | 100.31 | 510898 OKMULGE4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.03192 | 105.31 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.03192 | 111.62 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04556 | 113.94 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04823 | 116.57 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05163 | 112.39 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05174 | 110.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.16 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.2 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.22 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.23 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.29 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.29 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.29 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.31 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.32 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.34 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.34 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.42 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.42 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.43 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.49 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.51 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.52 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.59 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.59 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.6 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.62 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.63 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.7 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.73 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.78 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.8 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.8 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.8 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.82 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.96 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 110.98 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 111 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 111.03 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 111.04 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 111.04 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 111.13 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 111.13 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 111.24 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 111.24 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05182 | 112.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05183 | 111.02 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05183 | 111.02 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05183 | 111.02 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05184 | 110.51 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05184 | 110.51 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05184 | 110.51 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05185 | 110.34 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05185 | 110.53 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05185 | 112.6 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05186 | 110.3 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05186 | 110.31 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05188 | 110.45 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05188 | 110.46 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05196 | 114.25 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05199 | 110.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05202 | 110.33 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05206 | 110.93 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05206 | 110.93 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05206 | 110.93 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05208 | 111.08 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05208 | 111.16 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05208 | 111.16 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05215 | 111.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05218 | 110.53 | P23:345:WERE:WICH-345-116:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05243 | 111.14 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0525 | 110.27 | 300137 4BRISTOW 138 300686 4WOODY 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05259 | 112.85 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05264 | 115.7 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05264 | 115.76 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0532 | 113.88 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.054 | 117.46 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.054 | 117.51 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.054 | 117.51 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.054 | 117.51 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0542 | 117.76 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05486 | 120.04 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05777 | 112.93 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06172 | 114.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06172 | 114.39 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.03779 | 109.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-049 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.47 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.13692 | 100.9 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.13692 | 105.66 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 110.37 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 111.83 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-049 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.04342 | 105.21 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.04105 | 119.99 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05197 | 107.91 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05198 | 107.02 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05198 | 107.05 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05241 | 107.45 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05241 | 107.45 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05244 | 105.68 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05246 | 105.69 | P23:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0527 | 104.09 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05283 | 106.92 | P42:345:OKGE:SB_RARD7313:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05283 | 107.11 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05297 | 105.27 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05308 | 108.62 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05317 | 104.95 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05348 | 105.98 | P12:HV:EES::5HILLTOP%:NORFORK5!:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05353 | 104.73 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05356 | 105.48 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05356 | 105.48 | P21:161:EES-EAI:HRSN_E:EVRTON:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05356 | 105.54 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05356 | 105.55 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05356 | 105.55 | P21:161:EES-EAI:ST_JOE_E:HILTOP_E:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05357 | 105.16 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05357 | 105.31 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05379 | 104.37 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05382 | 104.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05383 | 104.16 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05383 | 104.16 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05384 | 104.29 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05386 | 104.29 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05387 | 104.11 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05387 | 104.28 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05387 | 104.3 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05389 | 104.19 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05391 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05391 | 104.12 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05391 | 104.14 | P12:345:XEL:ASAK-ECL SPS | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05391 | 104.16 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05391 | 104.19 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05392 | 104.06 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.06 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.07 | 655849 VEEDER -MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.08 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.08 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.08 | P13:069-161:OPPD:S1217 T1:LT::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.08 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.09 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.09 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.15 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.16 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.24 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.35 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.39 | P13:230:EES:NINEMI:AT4 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.41 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.49 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.5 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.53 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.73 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.76 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.82 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.84 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.89 | P11:HV:EES::1ISES U1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.93 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 104.93 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 105.46 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 105.51 | P13:161-22:AEPW:FLINTCR5:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 105.83 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 106.19 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 106.19 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 107.23 | 547498 STL439 5 161 547655 S1G439 1 13.2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 107.3 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 107.3 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 107.3 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 107.71 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 110.76 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 110.76 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05394 | 104.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05421 | 106.83 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05445 | 108.7 | Potential P4 Event - POI 774740_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05445 | 108.7 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05483 | 105.69 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05517 | 105.69 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05542 | 105.45 | P12:69:WERE:FRAN-NSES-69:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05609 | 105.03 | P23:345:AEPW:NES CB 3417B NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05609 | 105.03 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05624 | 108.91 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05637 | 105.35 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05654 | 107.08 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05654 | 108.16 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05783 | 106.14 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0624 | 108.65 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06435 | 114.33 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06983 | 112.05 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06983 | 112.07 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06997 | 110.97 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07096 | 111.3 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07096 | 111.3 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07156 | 119.48 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08832 | 125.69 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08832 | 125.7 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.11582 | 125.92 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-056 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03982 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-056 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03982 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-056 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03982 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-056 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.03974 | 102.17 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-057 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03135 | 125.92 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-057 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03568 | 125.69 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-057 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03568 | 125.7 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0332 | 247.85 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 209.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | Potential P4 Event - POI 525832_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04271 | 225.08 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04271 | 225.08 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04304 | 212.09 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.1 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.65 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.66 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.66 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.79 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04378 | 201.78 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0438 | 201.46 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04381 | 206.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04382 | 201.9 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04382 | 204.27 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04384 | 199.42 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04384 | 199.51 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 198.86 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:IPSCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.1 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.11 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.11 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.14 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.15 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | P12:EHV:EES::8SANS SOUCI%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.19 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EAI:NBF_SAN SO~1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.22 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.22 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.23 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.24 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.29 | P13:SH902T GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.3 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.34 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.35 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.36 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.41 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.44 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.46 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.51 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.53 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.53 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.63 | P23:345:XEL:8N8 MNN | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.64 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.67 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.73 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.74 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.8 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.86 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.86 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.89 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.91 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.92 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.06 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.09 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.09 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 201.31 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 201.31 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.07 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.08 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.08 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04412 | 210.59 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04582 | 209.74 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04927 | 232.94 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.05294 | 223.01 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03235 | 117.95 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.92 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03253 | 116.31 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 115.92 | Potential P4 Event - POI 776000_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 118.16 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03264 | 113.65 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03268 | 115.04 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03285 | 114.66 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 115.18 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 115.18 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.19 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.2 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.2 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.21 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.83 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.88 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.7 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.1 | ASGI-2021-003_POI_766051_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.25 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.4 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.4 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.62 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.62 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.67 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.67 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.69 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.69 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.7 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.73 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.73 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.97 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.97 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 113.18 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 113.18 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03357 | 116.56 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.04206 | 163.59 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03235 | 117.35 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03253 | 115.55 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 115.26 | Potential P4 Event - POI 773600_9 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 117.52 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03264 | 112.96 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03268 | 114.35 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03285 | 113.94 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 114.44 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 114.45 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.51 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.52 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.52 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.54 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.15 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.03 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.32 | ASGI-2021-003_POI_766051_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.49 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.63 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.65 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.88 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.88 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.89 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.89 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.9 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.91 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.91 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.93 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.93 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.94 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.94 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.98 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.02 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.02 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.27 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.27 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.45 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.45 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03357 | 115.94 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.04206 | 164.59 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-061 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06545 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-061 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06545 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-061 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06545 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-061 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0604 | 102.17 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-063 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.17244 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-063 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.17244 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-063 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.17244 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04276 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0448 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04484 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04484 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04484 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04484 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04484 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-063 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04484 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-064 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.05173 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-064 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.05173 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-064 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.05173 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-064 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.04294 | 102.17 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03206 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03206 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03206 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.03114 | 100.31 | 510898 OKMULGE4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.03114 | 105.31 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.03114 | 111.62 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.10216 | 102.19 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.10216 | 101.74 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23086 | 112.3 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23086 | 112.3 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 103.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 103.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 110.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 110.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 110.6 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 110.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23086 | 112.61 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23086 | 112.61 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 103.44 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 103.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 110.17 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 110.17 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 110.17 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23881 | 110.18 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.03423 | 119.99 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03322 | 107.91 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03363 | 107.02 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03363 | 107.05 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0338 | 107.45 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0338 | 107.45 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0341 | 105.68 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03413 | 105.69 | P23:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03433 | 106.92 | P42:345:OKGE:SB_RARD7313:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03433 | 107.11 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03462 | 104.09 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0353 | 104.95 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03561 | 104.73 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03568 | 105.98 | P12:HV:EES::5HILLTOP%:NORFORK5!:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03577 | 105.16 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03577 | 105.31 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03579 | 105.48 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03579 | 105.48 | P21:161:EES-EAI:HRSN_E:EVRTON:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03579 | 105.54 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03579 | 105.55 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03579 | 105.55 | P21:161:EES-EAI:ST_JOE_E:HILTOP_E:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03591 | 104.37 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03596 | 104.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03597 | 104.16 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03597 | 104.16 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03598 | 104.29 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03602 | 104.11 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03603 | 104.19 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03603 | 104.29 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03604 | 104.28 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03604 | 104.3 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03605 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 104.06 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 104.12 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 104.14 | P12:345:XEL:ASAK-ECL SPS | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 104.16 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 104.19 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 108.62 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.06 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.07 | 655849 VEEDER -MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.08 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.08 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.08 | P13:069-161:OPPD:S1217 T1:LT::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.08 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.09 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.09 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.15 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.16 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.24 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.35 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.39 | P13:230:EES:NINEMI:AT4 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.41 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.49 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.5 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.53 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.73 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.76 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.82 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.84 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.89 | P11:HV:EES::1ISES U1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.93 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.93 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 105.46 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 105.51 | P13:161-22:AEPW:FLINTCR5:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 105.83 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 106.19 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 106.19 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 107.23 | 547498 STL439 5 161 547655 S1G439 1 13.2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 107.3 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 107.3 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 107.3 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 107.71 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 110.76 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 110.76 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0361 | 104.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0361 | 105.27 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03657 | 106.83 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03686 | 108.7 | Potential P4 Event - POI 774740_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03686 | 108.7 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03687 | 105.69 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03705 | 105.69 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03725 | 105.45 | P12:69:WERE:FRAN-NSES-69:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03812 | 108.91 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03827 | 105.35 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03845 | 107.08 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03845 | 108.16 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03978 | 106.14 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0403 | 105.03 | P23:345:AEPW:NES CB 3417B NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0403 | 105.03 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04341 | 108.65 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04435 | 114.33 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05051 | 119.48 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06011 | 125.69 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06011 | 125.7 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0684 | 110.97 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06983 | 112.05 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06983 | 112.07 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07095 | 111.3 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07095 | 111.3 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08276 | 125.92 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.03423 | 119.99 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03322 | 107.91 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03363 | 107.02 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03363 | 107.05 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0338 | 107.45 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0338 | 107.45 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0341 | 105.68 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03413 | 105.69 | P23:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03433 | 106.92 | P42:345:OKGE:SB_RARD7313:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03433 | 107.11 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03462 | 104.09 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0353 | 104.95 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03561 | 104.73 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03568 | 105.98 | P12:HV:EES::5HILLTOP%:NORFORK5!:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03577 | 105.16 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03577 | 105.31 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03579 | 105.48 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03579 | 105.48 | P21:161:EES-EAI:HRSN_E:EVRTON:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03579 | 105.54 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03579 | 105.55 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03579 | 105.55 | P21:161:EES-EAI:ST_JOE_E:HILTOP_E:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03591 | 104.37 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03596 | 104.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03597 | 104.16 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03597 | 104.16 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03598 | 104.29 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03602 | 104.11 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03603 | 104.19 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03603 | 104.29 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03604 | 104.28 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03604 | 104.3 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03605 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 104.06 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 104.12 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 104.14 | P12:345:XEL:ASAK-ECL SPS | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 104.16 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 104.19 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03606 | 108.62 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.06 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.07 | 655849 VEEDER -MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.08 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.08 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.08 | P13:069-161:OPPD:S1217 T1:LT::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.08 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.09 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.09 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.15 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.16 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.24 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.35 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.39 | P13:230:EES:NINEMI:AT4 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.41 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.49 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.5 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.53 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.73 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.76 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.82 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.84 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.89 | P11:HV:EES::1ISES U1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.93 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 104.93 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 105.46 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 105.51 | P13:161-22:AEPW:FLINTCR5:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 105.83 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 106.19 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 106.19 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 107.23 | 547498 STL439 5 161 547655 S1G439 1 13.2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 107.3 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 107.3 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 107.3 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 107.71 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 110.76 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 110.76 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0361 | 104.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0361 | 105.27 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03657 | 106.83 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03686 | 108.7 | Potential P4 Event - POI 774740_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03686 | 108.7 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03687 | 105.69 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03705 | 105.69 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03725 | 105.45 | P12:69:WERE:FRAN-NSES-69:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03812 | 108.91 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03827 | 105.35 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03845 | 107.08 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03845 | 108.16 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03978 | 106.14 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0403 | 105.03 | P23:345:AEPW:NES CB 3417B NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0403 | 105.03 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04341 | 108.65 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04435 | 114.33 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05051 | 119.48 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06011 | 125.69 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06011 | 125.7 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0684 | 110.97 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06983 | 112.05 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06983 | 112.07 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07095 | 111.3 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07095 | 111.3 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08276 | 125.92 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-081 | FROM->TO | 527894 HOBBS_INT 6 230 997499 HICO 68759-1 230 1 | 528 | 607 | 0.14831 | 102.31 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | TDF Impact | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-081 | FROM->TO | 527896 HOBBS_INT 7 345 997499 HICO 68759-1 230 1 | 528 | 607 | 0.14831 | 103.84 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | TDF Impact | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-085 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03588 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-085 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03588 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-085 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03588 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 | 318.7 | 318.7 | 0.06831 | 100.58 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.52248 | 116.3 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.53231 | 120.17 | Potential P4 Event - POI 762216_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.53231 | 120.17 | Potential P4 Event - POI 762467_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.53231 | 120.26 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.53837 | 110.14 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.5412 | 112.66 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.5412 | 112.69 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.5412 | 112.69 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.5412 | 112.69 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.54975 | 104.1 | P12:115:SPS:T67_1_HAPPY_KRESS:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55207 | 103.02 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55421 | 102.5 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55489 | 103.74 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55489 | 103.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55489 | 103.84 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55496 | 103.74 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55618 | 106.31 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55618 | 106.85 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55618 | 106.85 | Potential P4 Event - POI 514801_3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55618 | 106.88 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.5563 | 102.05 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55666 | 102.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55666 | 104.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.5572 | 100.59 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55722 | 100.49 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55722 | 101.84 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55722 | 101.88 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.07 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.26 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.26 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.27 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.27 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.28 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.3 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.31 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.31 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.31 | 539800 CLARKCOUNTY7 345 763890 GEN-2019-058 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.31 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.32 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.32 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.32 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.32 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.32 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.32 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.32 | P23:500:EES:PERVIL:R9872 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.33 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.33 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.33 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.34 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.35 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.35 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.35 | P13:SH902T GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.35 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.36 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.36 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.36 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.38 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.38 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.4 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.42 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.43 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.44 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.46 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.46 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.47 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.48 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.48 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.5 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.51 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.53 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.54 | P23:345:XEL:8N8 MNN | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.56 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.56 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.6 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.6 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.6 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.62 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.62 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.64 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.65 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.65 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.67 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.7 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.7 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.72 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.73 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.74 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.8 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.8 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 100.98 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 101.13 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 101.13 | GEN-2023-015_POI_772280_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 101.16 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 101.16 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.55729 | 103.87 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13797 | 100.31 | 510898 OKMULGE4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13797 | 105.31 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13797 | 111.62 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.09138 | 102.19 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.09138 | 101.74 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.224 | 112.3 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.224 | 112.3 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 103.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 103.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 110.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 110.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 110.6 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 110.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.224 | 112.61 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.224 | 112.61 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 103.44 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 103.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 110.17 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 110.17 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 110.17 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.23637 | 110.18 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09825 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09825 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09825 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.12479 | 102.19 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.12479 | 101.74 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.25469 | 112.3 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.25469 | 112.3 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 103.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 103.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 110.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 110.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 110.6 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 110.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.25469 | 112.61 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.25469 | 112.61 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 103.44 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 103.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 110.17 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 110.17 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 110.17 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.26111 | 110.18 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-100 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.04513 | 109.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05594 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05594 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05715 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0577 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05944 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05944 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06288 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-100 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06317 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06035 | 120.04 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06827 | 117.46 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06827 | 117.51 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06827 | 117.51 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06827 | 117.51 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07186 | 117.76 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09156 | 113.88 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09402 | 112.85 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09765 | 132.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09765 | 132.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09765 | 132.22 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09765 | 132.22 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09765 | 135.65 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09765 | 135.66 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09765 | 135.69 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09765 | 135.71 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09765 | 149.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09908 | 112.39 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09973 | 111.02 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09973 | 111.02 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09973 | 111.02 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09974 | 116.57 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09996 | 110.53 | P23:345:WERE:WICH-345-116:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10014 | 110.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10021 | 111.08 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10021 | 111.16 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10021 | 111.16 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10024 | 114.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10024 | 114.39 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.16 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.2 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.22 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.23 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.29 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.29 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.29 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.3 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.31 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.31 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.32 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.34 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.34 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.42 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.42 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.43 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.49 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.51 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.52 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.59 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.59 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.6 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.62 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.63 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.7 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.73 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.78 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.8 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.8 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.8 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.82 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.96 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 110.98 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 111 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 111.03 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 111.04 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 111.04 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 111.13 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 111.13 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 111.24 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 111.24 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 112.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10028 | 112.6 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10029 | 110.34 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10029 | 110.45 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10029 | 110.46 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10029 | 110.51 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10029 | 110.51 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10029 | 110.51 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10029 | 110.53 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1003 | 110.27 | 300137 4BRISTOW 138 300686 4WOODY 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1003 | 110.33 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1003 | 110.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10031 | 110.93 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10031 | 110.93 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10031 | 110.93 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10032 | 111.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10035 | 111.14 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10239 | 113.94 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.103 | 112.93 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10311 | 115.7 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.10311 | 115.76 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.14278 | 114.25 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.09765 | 109.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-102 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.04513 | 109.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05594 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05594 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05715 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0577 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05944 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.05944 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06288 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-102 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06317 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.08454 | 102.19 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.08454 | 101.74 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 514898 CIMARON4 138 997829 CIMARON1 138 1 | 478 | 478 | 0.03022 | 105.83 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 514901 CIMARON7 345 997829 CIMARON1 138 1 | 478 | 478 | 0.03022 | 109.83 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.22359 | 112.3 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.22359 | 112.3 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 103.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 103.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 110.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 110.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 110.6 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 110.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.22359 | 112.61 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.22359 | 112.61 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 103.44 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 103.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 110.17 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 110.17 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 110.17 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.24979 | 110.18 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-132 | FROM->TO | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 205 | 205 | 1 | 109.93 | 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | TDF Impact | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.20383 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.20383 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.20383 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13186 | 100.31 | 510898 OKMULGE4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13186 | 105.31 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13186 | 111.62 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03363 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03389 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03403 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03403 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03403 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03403 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03403 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-134 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.03403 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.45266 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.45266 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.45266 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0332 | 247.85 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 209.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | Potential P4 Event - POI 525832_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04271 | 225.08 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04271 | 225.08 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04304 | 212.09 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.1 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.65 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.66 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.66 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.79 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04378 | 201.78 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0438 | 201.46 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04381 | 206.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04382 | 201.9 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04382 | 204.27 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04384 | 199.42 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04384 | 199.51 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 198.86 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:IPSCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.1 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.11 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.11 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.14 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.15 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | P12:EHV:EES::8SANS SOUCI%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.19 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EAI:NBF_SAN SO~1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.22 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.22 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.23 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.24 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.29 | P13:SH902T GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.3 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.34 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.35 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.36 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.41 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.44 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.46 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.51 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.53 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.53 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.63 | P23:345:XEL:8N8 MNN | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.64 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.67 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.73 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.74 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.8 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.86 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.86 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.89 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.91 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.92 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.06 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.09 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.09 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 201.31 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 201.31 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.07 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.08 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.08 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04412 | 210.59 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04582 | 209.74 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04927 | 232.94 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.05294 | 223.01 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03235 | 117.95 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.92 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03253 | 116.31 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 115.92 | Potential P4 Event - POI 776000_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 118.16 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03264 | 113.65 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03268 | 115.04 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03285 | 114.66 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 115.18 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 115.18 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.19 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.2 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.2 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.21 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.83 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.88 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.7 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.1 | ASGI-2021-003_POI_766051_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.25 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.4 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.4 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.62 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.62 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.67 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.67 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.69 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.69 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.7 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.73 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.73 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.97 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.97 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 113.18 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 113.18 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03357 | 116.56 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.04206 | 163.59 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03235 | 117.35 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03253 | 115.55 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 115.26 | Potential P4 Event - POI 773600_9 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 117.52 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03264 | 112.96 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03268 | 114.35 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03285 | 113.94 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 114.44 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 114.45 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.51 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.52 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.52 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.54 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.15 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.03 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.32 | ASGI-2021-003_POI_766051_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.49 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.63 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.65 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.88 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.88 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.89 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.89 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.9 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.91 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.91 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.93 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.93 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.94 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.94 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.98 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.02 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.02 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.27 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.27 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.45 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.45 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03357 | 115.94 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.04206 | 164.59 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0332 | 247.85 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 209.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04174 | 217.23 | Potential P4 Event - POI 525832_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04271 | 225.08 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04271 | 225.08 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04304 | 212.09 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.1 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04315 | 215.15 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.65 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.66 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.66 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04374 | 203.79 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04378 | 201.78 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0438 | 201.46 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04381 | 206.93 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04382 | 201.9 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04382 | 204.27 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04384 | 199.42 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04384 | 199.51 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 198.86 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:IPSCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.1 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.11 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.11 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.14 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.15 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.17 | P12:EHV:EES::8SANS SOUCI%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.19 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.2 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EAI:NBF_SAN SO~1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.21 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.22 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.22 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.23 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.24 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.27 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.29 | P13:SH902T GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.3 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.31 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.33 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.34 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.35 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.36 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.41 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.44 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.44 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.46 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.51 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.53 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.53 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.62 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.63 | P23:345:XEL:8N8 MNN | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.64 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.67 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.69 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.73 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.74 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.77 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.8 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.85 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.86 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.86 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.89 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.91 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 199.92 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.06 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.09 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 200.09 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 201.31 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 201.31 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.07 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.08 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04385 | 211.08 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04412 | 210.59 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04582 | 209.74 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04927 | 232.94 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.05294 | 223.01 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03235 | 117.95 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.92 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.93 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03253 | 116.31 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 115.92 | Potential P4 Event - POI 776000_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 118.16 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03264 | 113.65 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03268 | 115.04 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03285 | 114.66 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 115.18 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 115.18 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.19 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.2 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.2 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 113.21 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.83 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.88 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.7 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.1 | ASGI-2021-003_POI_766051_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.25 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.39 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.4 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.4 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.61 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.62 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.62 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.64 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.65 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.66 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.67 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.67 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.68 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.69 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.69 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.7 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.73 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.73 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.97 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.97 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 113.18 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 113.18 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.03357 | 116.56 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.04206 | 163.59 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03235 | 117.35 | Potential P4 Event - POI 526936_3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 525832_5 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03244 | 117.32 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03253 | 115.55 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 115.26 | Potential P4 Event - POI 773600_9 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.0326 | 117.52 | Potential P4 Event - POI 776000_0 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03264 | 112.96 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03268 | 114.35 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03285 | 113.94 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 114.44 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03286 | 114.45 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.51 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.52 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.52 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03293 | 112.54 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.15 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 112.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03294 | 113.03 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.32 | ASGI-2021-003_POI_766051_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.49 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.63 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.64 | P13:138-230:AEPW:ELKCTY-4:::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.65 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.88 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.88 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.89 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.89 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.9 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.91 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.91 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.92 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.93 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.93 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.94 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.94 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.95 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.97 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 111.98 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.02 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.02 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.27 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.27 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.45 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03295 | 112.45 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.03357 | 115.94 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.04206 | 164.59 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.29658 | 102.17 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542965 W.GRDNR7 345 997212 WEST GARDN11 161 11 | 535 | 535 | 0.09635 | 102.38 | Potential P4 Event - POI 542940_3 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542965 W.GRDNR7 345 997212 WEST GARDN11 161 11 | 535 | 535 | 0.09635 | 106.21 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542965 W.GRDNR7 345 997212 WEST GARDN11 161 11 | 535 | 535 | 0.11927 | 109.33 | Potential P4 Event - POI 542965_4 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.05795 | 109.02 | Potential P4 Event - POI 542940_3 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.05795 | 112.07 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.06827 | 108.15 | Potential P4 Event - POI 542965_4 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 | 311 | 334 | 0.03485 | 100.93 | Potential P4 Event - POI 542940_3 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 | 311 | 334 | 0.03485 | 102.91 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 | 311 | 334 | 0.04362 | 105.73 | Potential P4 Event - POI 542965_4 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 997212 WEST GARDN11 161 11 | 535 | 535 | 0.09635 | 101.7 | Potential P4 Event - POI 542940_3 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 997212 WEST GARDN11 161 11 | 535 | 535 | 0.09635 | 105.38 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 997212 WEST GARDN11 161 11 | 535 | 535 | 0.11927 | 108.29 | Potential P4 Event - POI 542965_4 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 311 | 334 | 0.09032 | 100.26 | 541340 BELTONS5 161 541342 PECULR 5 161 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 311 | 334 | 0.13733 | 113.16 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1 | 311 | 334 | 0.04194 | 101.89 | 543036 OLATHE 5 161 543045 SWITZER5 161 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 | 311 | 334 | 0.13733 | 104.46 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 543044 MOONLT 5 161 543132 BNSF 5 161 1 | 311 | 334 | 0.04362 | 101.37 | Potential P4 Event - POI 542965_4 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.06731 | 101.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.06751 | 101.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.06751 | 101.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.06792 | 101.62 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.06792 | 101.62 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.10639 | 109.43 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.10728 | 109.43 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.10728 | 109.43 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.10804 | 109.45 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.10804 | 109.45 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.1095 | 104.01 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.1095 | 104.01 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11277 | 106.73 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.10639 | 117.94 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.10728 | 117.94 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.10728 | 117.94 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.10804 | 117.97 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.10804 | 117.97 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.1095 | 111.97 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.1095 | 111.97 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11277 | 114.99 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0531 | 103.32 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05905 | 100.96 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05905 | 100.96 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05905 | 103.59 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05905 | 103.61 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05905 | 110.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06919 | 117.26 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06919 | 119.07 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06919 | 120.23 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07125 | 139.6 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07146 | 139.59 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07146 | 139.59 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07189 | 139.62 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07189 | 139.62 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07246 | 115.17 | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07246 | 116.23 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07253 | 135.18 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07253 | 135.18 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07355 | 136.74 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.10639 | 127.39 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.10728 | 127.38 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.10728 | 127.38 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.10804 | 127.4 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.10804 | 127.4 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.1095 | 121.82 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.1095 | 121.82 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11277 | 124.55 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05285 | 114.01 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0531 | 121.97 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.49 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.51 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.74 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.75 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.75 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.76 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.77 | P13:230:EES:NINEMI:AT4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.78 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.78 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.78 | P13:230:EES:NINEMI:AT5 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.79 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.79 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.79 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.81 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.81 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.82 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.84 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.88 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.89 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.89 | P11:HV:EES::1ISES U1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.9 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.91 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.91 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.91 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.94 | P11:25:EES:WATERF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.94 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 107.94 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 108.24 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 108.26 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 108.34 | 775520 G23-177-TAP 138 775521 GEN-2023-177 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 108.59 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 108.63 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 108.63 | GEN-2022-238_POI_515055_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 108.76 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 108.83 | 774660 G23-134-TAP 138 774661 GEN-2023-134 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 108.83 | 774661 GEN-2023-134 138 774662 G23-134XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05397 | 108.84 | GEN-2023-134_POI_774660_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05398 | 107.74 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05398 | 107.75 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05398 | 107.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05398 | 107.85 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05398 | 107.87 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05398 | 108.21 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05398 | 108.22 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05399 | 107.92 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05399 | 107.92 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05399 | 108.08 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05399 | 108.2 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.054 | 108.37 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.054 | 108.4 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.054 | 108.4 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05402 | 109.04 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0541 | 108.82 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05422 | 109.27 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05423 | 110.21 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0545 | 107.9 | P12:138:OKGE-WFEC:BKRBKR368_1:27S_32S::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0545 | 107.9 | P12:138:WFEC:ANADRKO_GRCMNT_2:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05453 | 109.42 | P12:138:OKGE:BKRBKR95:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05846 | 115.26 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05905 | 119.94 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05905 | 119.94 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05905 | 122.63 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05905 | 122.66 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05905 | 129.53 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06271 | 117.31 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06919 | 136.12 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06919 | 138.02 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06919 | 139.22 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07125 | 159.23 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07146 | 159.21 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07146 | 159.21 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07189 | 159.25 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07189 | 159.25 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07246 | 133.99 | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07246 | 135.07 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07253 | 154.69 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07253 | 154.69 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07355 | 156.31 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.10639 | 114.59 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.10728 | 114.58 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.10728 | 114.58 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.10804 | 114.6 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.10804 | 114.6 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.1095 | 109.11 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.1095 | 109.11 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11277 | 111.84 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34254 | 114.25 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34543 | 110.34 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.16 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.2 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.22 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.23 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.27 | 300137 4BRISTOW 138 300686 4WOODY 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.29 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.29 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.29 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.3 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.31 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.31 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.32 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.34 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.34 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.42 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.42 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.43 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.49 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.51 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.51 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.51 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.51 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.52 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.53 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.59 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.59 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.6 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.62 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.63 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.7 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.73 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.78 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.8 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.8 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.8 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.82 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.96 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 110.98 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 111 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 111.03 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 111.04 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 111.04 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 111.13 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 111.13 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 111.24 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 111.24 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 112.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34544 | 112.6 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34545 | 110.45 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34545 | 110.46 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34549 | 110.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3455 | 110.33 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34551 | 110.93 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34551 | 110.93 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34551 | 110.93 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34553 | 110.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34557 | 111.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34563 | 111.14 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34566 | 110.53 | P23:345:WERE:WICH-345-116:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3457 | 111.02 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3457 | 111.02 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3457 | 111.02 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34577 | 111.08 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34577 | 111.16 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34577 | 111.16 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34607 | 112.39 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34818 | 112.85 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35054 | 113.88 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35214 | 117.46 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35214 | 117.51 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35214 | 117.51 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35214 | 117.51 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35331 | 117.76 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35518 | 120.04 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35841 | 114.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35841 | 114.39 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.36018 | 116.57 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.36494 | 113.94 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.37075 | 112.93 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.37272 | 115.7 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.37272 | 115.76 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.43009 | 132.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.43009 | 132.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.43009 | 132.22 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.43009 | 132.22 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.43009 | 135.65 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.43009 | 135.66 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.43009 | 135.69 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.43009 | 135.71 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.43009 | 149.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.45114 | 109.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03494 | 101.09 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03494 | 102.6 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03494 | 105.49 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03494 | 111.25 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03494 | 112.75 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03494 | 115.66 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03496 | 106.64 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03496 | 108.22 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03496 | 109.36 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03037 | 102.64 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03037 | 102.89 | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03037 | 102.95 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03053 | 107.49 | Potential P4 Event - POI 515497_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03273 | 105.2 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03273 | 105.41 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03273 | 105.41 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03273 | 105.97 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03273 | 105.98 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03273 | 106.79 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03273 | 106.79 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03322 | 105.39 | P42:345:OKGE:SB_CION7383:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03496 | 117.41 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03496 | 118.99 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03496 | 120.13 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 515135 SUNNYSD4 138 997801 SUNNYSD3 138 3 | 330 | 330 | 0.038 | 104.14 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.27657 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.27657 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.27778 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.27978 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.28008 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.28008 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.28352 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.29782 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 515136 SUNNYSD7 345 997801 SUNNYSD3 138 3 | 330 | 330 | 0.038 | 103.47 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.08566 | 103.38 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.08566 | 103.38 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.08566 | 105.84 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.08566 | 105.86 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.08566 | 111.67 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.08589 | 101.2 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.09099 | 107.06 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.09099 | 107.08 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.09099 | 107.4 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.09258 | 111.39 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.09258 | 113.9 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.09353 | 109.91 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.09353 | 113.85 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.10159 | 143.77 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.10182 | 143.76 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.10182 | 143.76 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.10182 | 143.76 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.10236 | 143.74 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.10314 | 139.27 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.1053 | 141.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.11115 | 139.27 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.07899 | 101.21 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08566 | 107.11 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08566 | 107.11 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08566 | 109.58 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08566 | 109.59 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08566 | 115.42 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.08589 | 104.92 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.09099 | 110.78 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.09099 | 110.8 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.09099 | 111.12 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.09258 | 115.12 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.09258 | 117.63 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.09353 | 113.61 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.09353 | 117.56 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10159 | 147.54 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10182 | 147.53 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10182 | 147.53 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10182 | 147.53 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10236 | 147.51 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.10314 | 143.04 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.1053 | 145.38 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.11115 | 143.04 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08566 | 102.38 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08566 | 102.39 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08566 | 108.18 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.09099 | 103.61 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.09099 | 103.63 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.09099 | 103.95 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.09258 | 107.93 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.09258 | 110.43 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.09353 | 106.46 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.09353 | 110.39 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10159 | 140.23 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10182 | 140.22 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10182 | 140.22 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10182 | 140.22 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10236 | 140.2 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.10314 | 135.75 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.1053 | 138.07 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.11115 | 135.75 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10259 | 106.45 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10286 | 106.43 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10286 | 106.43 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10286 | 106.43 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10349 | 106.43 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10442 | 102.72 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10442 | 102.72 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.10678 | 104.53 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10259 | 114.05 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10286 | 114.04 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10286 | 114.04 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10286 | 114.04 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10349 | 114.03 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10442 | 110.29 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10442 | 110.29 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.10678 | 112.1 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.07176 | 102.72 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.07176 | 102.73 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.07176 | 111.27 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08091 | 123.24 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08093 | 123.23 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08093 | 123.23 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08147 | 123.24 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08147 | 123.24 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08212 | 119.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08212 | 119.34 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08366 | 121.01 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.07176 | 100.22 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.07176 | 100.23 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.07176 | 108.76 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08091 | 120.69 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08093 | 120.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08093 | 120.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08147 | 120.69 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08147 | 120.69 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08212 | 116.8 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08212 | 116.8 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08366 | 118.46 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10259 | 122.01 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10286 | 122 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10286 | 122 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10286 | 122 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10349 | 122 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10442 | 118.22 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10442 | 118.22 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.10678 | 120.05 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10259 | 120.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10286 | 120.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10286 | 120.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10286 | 120.11 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10349 | 120.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10442 | 116.33 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10442 | 116.33 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10678 | 118.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10259 | 120.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10286 | 120.1 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10286 | 120.1 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10286 | 120.1 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10349 | 120.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10442 | 116.33 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10442 | 116.33 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-150 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.10678 | 118.15 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.23594 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.23594 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.23594 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.04845 | 109.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.12632 | 101.09 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.12632 | 102.6 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.12632 | 105.49 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.12632 | 111.25 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.12632 | 112.75 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.12632 | 115.66 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.0878 | 104.09 | P12:138:OKGE:BKRBKR125:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.12416 | 106.64 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.12416 | 108.22 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.12416 | 109.36 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0878 | 114.94 | P12:138:OKGE:BKRBKR125:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09219 | 102.46 | P12:138:WFEC:FRANKLN_MIDWEST:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.25 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.26 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.32 | P13:19-345:XEL:AUTO-SINGLE:MEC-ST:MEC-345:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.33 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.33 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.33 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.34 | P11:115:XEL:HBR #7 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.35 | 562021 G11-020-SUB 345 562024 G11-019-SUB 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.35 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.35 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.35 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.35 | P12:230:UMZ:# 20119 #:: PROPER N-1 FOR DRYCREEK4:HV: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.35 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.35 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.35 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.56 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.57 | 587211 G16-032XFMR1 34.5 587210 GEN-2016-032 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.57 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.58 | P13:138:EES:LC:T2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.61 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.62 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.62 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.64 | 505522 VAN BUR5 161 773101 GEN-2023-056 161 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.65 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.65 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.67 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.7 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.73 | 508298 LYDIA 7 345 764075 GEN-2020-054 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.74 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.75 | P13:230:EES:NINEMI:AT4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.76 | P13:230:EES:NINEMI:AT5 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.77 | P11:18:EES-EAI:ETTA:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.77 | P11:EHV:EES::1DUKE HS S1:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.79 | P11:16:EES-EAI:MAGNET:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.79 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.8 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.8 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.84 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.86 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.97 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 100.98 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 101.03 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 101.03 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 101.1 | P11:25:EES:WATERF:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 101.1 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 101.1 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 101.25 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 101.28 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 101.28 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 101.34 | 774660 G23-134-TAP 138 774661 GEN-2023-134 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 101.94 | 776180 G23-210-TAP 138 776181 GEN-2023-210 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 107.02 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 107.02 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 107.91 | 775341 GEN-2023-168 138 775342 G23-168XFMR1 34.5 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09279 | 107.91 | GEN-2023-168_POI_514922_Generator_outage | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0928 | 100.26 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0928 | 100.28 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0928 | 100.59 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0928 | 100.78 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09281 | 100.59 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09281 | 100.76 | 300138 4CLEVLND 138 512729 CLEVLND 4 138 Z1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09282 | 100.85 | P23:345:WERE:WAVS-BKRS:::EHV: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09282 | 101.27 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09283 | 100.85 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09283 | 100.91 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09283 | 101.07 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09284 | 101.04 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09284 | 101.04 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09285 | 101.07 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09286 | 101.3 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09286 | 101.3 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09286 | 101.53 | Potential P4 Event - POI 531449_3 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09287 | 101.08 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09287 | 101.35 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09289 | 101.59 | Potential P4 Event - POI 531449_0 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09291 | 100.79 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09291 | 101 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09296 | 102.64 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09296 | 102.89 | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09296 | 102.95 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.093 | 101.36 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09303 | 101.23 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0942 | 105.5 | P12:345:OKGE:BKRBKR443NEW3:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0955 | 105.2 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0955 | 105.41 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0955 | 105.41 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0955 | 105.97 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0955 | 105.98 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0955 | 106.79 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0955 | 106.79 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09598 | 101.29 | 520893 EL RENO4 138 3WXFMR EL RENO 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09635 | 107.49 | Potential P4 Event - POI 515497_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.09684 | 105.39 | P42:345:OKGE:SB_CION7383:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.12416 | 117.41 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.12416 | 118.99 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.12416 | 120.13 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06638 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06638 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06646 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06759 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06988 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.06988 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0729 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-161 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.07332 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.04488 | 101.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.04508 | 101.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.04508 | 101.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.04548 | 101.62 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.04548 | 101.62 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.07942 | 109.43 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08031 | 109.43 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08031 | 109.43 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08107 | 109.45 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08107 | 109.45 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08253 | 104.01 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08253 | 104.01 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.0891 | 106.73 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.07942 | 117.94 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08031 | 117.94 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08031 | 117.94 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08107 | 117.97 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08107 | 117.97 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08253 | 111.97 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08253 | 111.97 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.0891 | 114.99 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04751 | 139.6 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04772 | 139.59 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04772 | 139.59 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04814 | 139.62 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04814 | 139.62 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04878 | 135.18 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04878 | 135.18 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05084 | 136.74 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.07942 | 127.39 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08031 | 127.38 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08031 | 127.38 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08107 | 127.4 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08107 | 127.4 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08253 | 121.82 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08253 | 121.82 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.0891 | 124.55 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03372 | 125.38 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0339 | 125.37 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0339 | 125.37 | Potential P4 Event - POI 514801_4 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0342 | 125.43 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0342 | 125.43 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03466 | 122.73 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03814 | 124.73 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04751 | 159.23 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04772 | 159.21 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04772 | 159.21 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04814 | 159.25 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04814 | 159.25 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04878 | 154.69 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04878 | 154.69 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05084 | 156.31 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03372 | 115.9 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0339 | 115.9 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0339 | 115.9 | Potential P4 Event - POI 514801_3 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0342 | 115.95 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0342 | 115.95 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03466 | 113.47 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03814 | 115.31 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.07942 | 114.59 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08031 | 114.58 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08031 | 114.58 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08107 | 114.6 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08107 | 114.6 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08253 | 109.11 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08253 | 109.11 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.0891 | 111.84 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49609 | 110.27 | 300137 4BRISTOW 138 300686 4WOODY 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49612 | 110.34 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49612 | 112.6 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.16 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.2 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.22 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.23 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.29 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.29 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.29 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.3 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.31 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.31 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.32 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.34 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.34 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.42 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.42 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.43 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.49 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.51 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.51 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.51 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.51 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.52 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.53 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.59 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.59 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.6 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.62 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.63 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.7 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.73 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.78 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.8 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.8 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.8 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.82 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.96 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.98 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.03 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.04 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.04 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.13 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.13 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.24 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.24 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 112.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49614 | 110.45 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49614 | 110.46 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49618 | 110.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49619 | 110.33 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4962 | 110.93 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4962 | 110.93 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4962 | 110.93 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49624 | 110.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49626 | 111.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49631 | 111.14 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49634 | 110.53 | P23:345:WERE:WICH-345-116:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49643 | 111.02 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49643 | 111.02 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49643 | 111.02 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49648 | 111.08 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49648 | 111.16 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49648 | 111.16 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49685 | 112.39 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49916 | 112.85 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5017 | 113.88 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5037 | 114.25 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50397 | 117.46 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50397 | 117.51 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50397 | 117.51 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50397 | 117.51 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50442 | 113.94 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5051 | 117.76 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50614 | 112.93 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50736 | 120.04 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50793 | 115.7 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50793 | 115.76 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50987 | 114.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50987 | 114.39 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.51341 | 116.57 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 132.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 132.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 132.22 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 132.22 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 135.65 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 135.66 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 135.69 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 135.71 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 149.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.61651 | 109.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03143 | 101.09 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03143 | 102.6 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03143 | 105.49 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03143 | 111.25 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03143 | 112.75 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03143 | 115.66 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03455 | 106.64 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03455 | 108.22 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03455 | 109.36 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03227 | 107.49 | Potential P4 Event - POI 515497_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03455 | 117.41 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03455 | 118.99 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03455 | 120.13 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 105.2 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 105.41 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 105.41 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 105.97 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 105.98 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 106.79 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 106.79 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0358 | 105.39 | P42:345:OKGE:SB_CION7383:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515135 SUNNYSD4 138 997801 SUNNYSD3 138 3 | 330 | 330 | 0.04619 | 104.14 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35438 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35448 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35448 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35569 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35798 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35798 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.36142 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.39017 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515136 SUNNYSD7 345 997801 SUNNYSD3 138 3 | 330 | 330 | 0.04619 | 103.47 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.27376 | 110.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.6 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.28041 | 103.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.28041 | 103.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.33054 | 112.3 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.33054 | 112.3 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.27376 | 110.18 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.17 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.17 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.17 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.28041 | 103.44 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.28041 | 103.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.33054 | 112.61 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.33054 | 112.61 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03056 | 101.2 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03333 | 107.06 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03333 | 107.08 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03333 | 107.4 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03384 | 111.39 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03384 | 113.9 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03424 | 109.91 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03424 | 113.85 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03513 | 103.38 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03513 | 103.38 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03513 | 105.84 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03513 | 105.86 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03513 | 111.67 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05956 | 143.77 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05979 | 143.76 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05979 | 143.76 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05979 | 143.76 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06033 | 143.74 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06111 | 139.27 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06545 | 141.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.07756 | 139.27 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03056 | 104.92 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03073 | 101.21 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03333 | 110.78 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03333 | 110.8 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03333 | 111.12 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03384 | 115.12 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03384 | 117.63 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03424 | 113.61 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03424 | 117.56 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03513 | 107.11 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03513 | 107.11 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03513 | 109.58 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03513 | 109.59 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03513 | 115.42 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05956 | 147.54 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05979 | 147.53 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05979 | 147.53 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05979 | 147.53 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06033 | 147.51 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06111 | 143.04 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06545 | 145.38 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.07756 | 143.04 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03333 | 103.61 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03333 | 103.63 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03333 | 103.95 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03384 | 107.93 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03384 | 110.43 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03424 | 106.46 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03424 | 110.39 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03513 | 102.38 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03513 | 102.39 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03513 | 108.18 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05956 | 140.23 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05979 | 140.22 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05979 | 140.22 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05979 | 140.22 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06033 | 140.2 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06111 | 135.75 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06545 | 138.07 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.07756 | 135.75 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.06978 | 106.45 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07005 | 106.43 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07005 | 106.43 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07005 | 106.43 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07068 | 106.43 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.0716 | 102.72 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.0716 | 102.72 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07636 | 104.53 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.06978 | 114.05 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07005 | 114.04 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07005 | 114.04 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07005 | 114.04 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07068 | 114.03 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.0716 | 110.29 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.0716 | 110.29 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07636 | 112.1 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04253 | 102.72 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04253 | 102.73 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04253 | 111.27 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05837 | 123.24 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05839 | 123.23 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05839 | 123.23 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05893 | 123.24 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05893 | 123.24 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05958 | 119.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05958 | 119.34 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06268 | 121.01 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04253 | 100.22 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04253 | 100.23 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04253 | 108.76 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05837 | 120.69 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05839 | 120.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05839 | 120.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05893 | 120.69 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05893 | 120.69 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05958 | 116.8 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05958 | 116.8 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.06268 | 118.46 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.06978 | 122.01 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07005 | 122 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07005 | 122 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07005 | 122 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07068 | 122 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.0716 | 118.22 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.0716 | 118.22 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07636 | 120.05 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06978 | 120.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.11 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07068 | 120.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0716 | 116.33 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0716 | 116.33 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07636 | 118.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06978 | 120.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.1 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.1 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.1 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07068 | 120.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0716 | 116.33 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0716 | 116.33 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-164 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07636 | 118.15 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.04488 | 101.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.04508 | 101.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.04508 | 101.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.04548 | 101.62 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.04548 | 101.62 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.07942 | 109.43 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08031 | 109.43 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08031 | 109.43 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08107 | 109.45 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08107 | 109.45 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08253 | 104.01 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.08253 | 104.01 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.0891 | 106.73 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.07942 | 117.94 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08031 | 117.94 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08031 | 117.94 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08107 | 117.97 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08107 | 117.97 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08253 | 111.97 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.08253 | 111.97 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.0891 | 114.99 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04751 | 139.6 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04772 | 139.59 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04772 | 139.59 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04814 | 139.62 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04814 | 139.62 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04878 | 135.18 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04878 | 135.18 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05084 | 136.74 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.07942 | 127.39 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08031 | 127.38 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08031 | 127.38 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08107 | 127.4 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08107 | 127.4 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08253 | 121.82 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.08253 | 121.82 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.0891 | 124.55 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03372 | 125.38 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0339 | 125.37 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0339 | 125.37 | Potential P4 Event - POI 514801_4 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0342 | 125.43 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0342 | 125.43 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03466 | 122.73 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03814 | 124.73 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04751 | 159.23 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04772 | 159.21 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04772 | 159.21 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04814 | 159.25 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04814 | 159.25 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04878 | 154.69 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.04878 | 154.69 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.05084 | 156.31 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03372 | 115.9 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0339 | 115.9 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0339 | 115.9 | Potential P4 Event - POI 514801_3 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0342 | 115.95 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0342 | 115.95 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03466 | 113.47 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03814 | 115.31 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.07942 | 114.59 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08031 | 114.58 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08031 | 114.58 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08107 | 114.6 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08107 | 114.6 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08253 | 109.11 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.08253 | 109.11 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.0891 | 111.84 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49609 | 110.27 | 300137 4BRISTOW 138 300686 4WOODY 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49612 | 110.34 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49612 | 112.6 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.16 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.2 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.22 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.23 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.29 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.29 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.29 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.3 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.31 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.31 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.32 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.34 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.34 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.42 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.42 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.43 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.49 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.51 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.51 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.51 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.51 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.52 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.53 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.59 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.59 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.6 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.62 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.63 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.7 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.73 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.78 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.8 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.8 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.8 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.82 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.96 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 110.98 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.03 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.04 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.04 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.13 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.13 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.24 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 111.24 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49613 | 112.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49614 | 110.45 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49614 | 110.46 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49618 | 110.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49619 | 110.33 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4962 | 110.93 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4962 | 110.93 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4962 | 110.93 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49624 | 110.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49626 | 111.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49631 | 111.14 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49634 | 110.53 | P23:345:WERE:WICH-345-116:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49643 | 111.02 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49643 | 111.02 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49643 | 111.02 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49648 | 111.08 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49648 | 111.16 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49648 | 111.16 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49685 | 112.39 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49916 | 112.85 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5017 | 113.88 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5037 | 114.25 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50397 | 117.46 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50397 | 117.51 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50397 | 117.51 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50397 | 117.51 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50442 | 113.94 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5051 | 117.76 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50614 | 112.93 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50736 | 120.04 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50793 | 115.7 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50793 | 115.76 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50987 | 114.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50987 | 114.39 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.51341 | 116.57 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 132.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 132.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 132.22 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 132.22 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 135.65 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 135.66 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 135.69 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 135.71 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59546 | 149.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.61651 | 109.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03143 | 101.09 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03143 | 102.6 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03143 | 105.49 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03143 | 111.25 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03143 | 112.75 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03143 | 115.66 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03455 | 106.64 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03455 | 108.22 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03455 | 109.36 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03227 | 107.49 | Potential P4 Event - POI 515497_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03455 | 117.41 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03455 | 118.99 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03455 | 120.13 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 105.2 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 105.41 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 105.41 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 105.97 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 105.98 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 106.79 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03466 | 106.79 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.0358 | 105.39 | P42:345:OKGE:SB_CION7383:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515135 SUNNYSD4 138 997801 SUNNYSD3 138 3 | 330 | 330 | 0.04619 | 104.14 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35438 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35448 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35448 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35569 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35798 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.35798 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.36142 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.39017 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515136 SUNNYSD7 345 997801 SUNNYSD3 138 3 | 330 | 330 | 0.04619 | 103.47 | P13:138-345:OKGE:BKRBKR_3W045:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.27376 | 110.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.6 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.28041 | 103.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.28041 | 103.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.33054 | 112.3 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.33054 | 112.3 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.27376 | 110.18 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.17 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.17 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.27439 | 110.17 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.28041 | 103.44 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.28041 | 103.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.33054 | 112.61 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.33054 | 112.61 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03056 | 101.2 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03333 | 107.06 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03333 | 107.08 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03333 | 107.4 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03384 | 111.39 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03384 | 113.9 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03424 | 109.91 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03424 | 113.85 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03513 | 103.38 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03513 | 103.38 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03513 | 105.84 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03513 | 105.86 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03513 | 111.67 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05956 | 143.77 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05979 | 143.76 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05979 | 143.76 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05979 | 143.76 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06033 | 143.74 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06111 | 139.27 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06545 | 141.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.07756 | 139.27 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03056 | 104.92 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03073 | 101.21 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03333 | 110.78 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03333 | 110.8 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03333 | 111.12 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03384 | 115.12 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03384 | 117.63 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03424 | 113.61 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03424 | 117.56 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03513 | 107.11 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03513 | 107.11 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03513 | 109.58 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03513 | 109.59 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03513 | 115.42 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05956 | 147.54 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05979 | 147.53 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05979 | 147.53 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05979 | 147.53 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06033 | 147.51 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06111 | 143.04 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06545 | 145.38 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.07756 | 143.04 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03333 | 103.61 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03333 | 103.63 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03333 | 103.95 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03384 | 107.93 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03384 | 110.43 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03424 | 106.46 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03424 | 110.39 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03513 | 102.38 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03513 | 102.39 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03513 | 108.18 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05956 | 140.23 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05979 | 140.22 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05979 | 140.22 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05979 | 140.22 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06033 | 140.2 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06111 | 135.75 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06545 | 138.07 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.07756 | 135.75 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.06978 | 106.45 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07005 | 106.43 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07005 | 106.43 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07005 | 106.43 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07068 | 106.43 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.0716 | 102.72 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.0716 | 102.72 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.07636 | 104.53 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.06978 | 114.05 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07005 | 114.04 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07005 | 114.04 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07005 | 114.04 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07068 | 114.03 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.0716 | 110.29 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.0716 | 110.29 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.07636 | 112.1 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04253 | 102.72 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04253 | 102.73 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04253 | 111.27 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05837 | 123.24 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05839 | 123.23 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05839 | 123.23 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05893 | 123.24 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05893 | 123.24 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05958 | 119.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05958 | 119.34 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06268 | 121.01 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04253 | 100.22 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04253 | 100.23 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04253 | 108.76 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05837 | 120.69 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05839 | 120.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05839 | 120.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05893 | 120.69 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05893 | 120.69 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05958 | 116.8 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.05958 | 116.8 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.06268 | 118.46 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.06978 | 122.01 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07005 | 122 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07005 | 122 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07005 | 122 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07068 | 122 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.0716 | 118.22 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.0716 | 118.22 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.07636 | 120.05 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06978 | 120.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.11 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07068 | 120.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0716 | 116.33 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0716 | 116.33 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07636 | 118.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.06978 | 120.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.1 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.1 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07005 | 120.1 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07068 | 120.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0716 | 116.33 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0716 | 116.33 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-165 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.07636 | 118.15 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-168 | FROM->TO | 514868 DOUGLTP4 138 514922 CLASSEN4 138 1 | 268 | 287 | 0.3814 | 115.61 | 514861 MUSTANG4 138 514865 COUNCIL4 138 1 | TDF Impact | Multi - West Oaks - Council - Classen 138 kV Reconductor
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-169 | FROM->TO | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 187 | 211 | 0.94226 | 118.87 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-169 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 199 | 223 | 0.94228 | 116.33 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03098 | 111.02 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03098 | 111.02 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0338 | 111.02 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 531379 JONES3 115 531426 JAMESON3 115 1 | 119.5 | 148.2 | 0.07684 | 100.26 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 531379 JONES3 115 531448 HOLCOMB3 115 1 | 119.5 | 148.2 | 0.07684 | 106.23 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 355 | 355 | 0.05103 | 103.01 | Potential P4 Event - POI 531449_2 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.03102 | 113.68 | Potential P4 Event - POI 531449_2 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 531419 DOBSON 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.17192 | 112.38 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 531420 FLETCHR3 115 531440 WILLIAM3 115 1 | 99.6 | 99.6 | 0.05732 | 101.17 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 211.7 | 229 | 0.17192 | 109.63 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 531432 PILE 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.17192 | 111.35 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 195.4 | 195.4 | 0.11141 | 113.12 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-172 | FROM->TO | 531449 HOLCOMB7 345 997448 HOLCOMB 115 1 | 336 | 358.5 | 0.36671 | 100.11 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03098 | 111.02 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03098 | 111.02 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0338 | 111.02 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 531379 JONES3 115 531426 JAMESON3 115 1 | 119.5 | 148.2 | 0.07684 | 100.26 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 531379 JONES3 115 531448 HOLCOMB3 115 1 | 119.5 | 148.2 | 0.07684 | 106.23 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 355 | 355 | 0.05103 | 103.01 | Potential P4 Event - POI 531449_2 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 153.4 | 165.1 | 0.03102 | 113.68 | Potential P4 Event - POI 531449_2 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 531419 DOBSON 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.17192 | 112.38 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 531420 FLETCHR3 115 531440 WILLIAM3 115 1 | 99.6 | 99.6 | 0.05732 | 101.17 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 211.7 | 229 | 0.17192 | 109.63 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 531432 PILE 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.17192 | 111.35 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 195.4 | 195.4 | 0.11141 | 113.12 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-173 | FROM->TO | 531449 HOLCOMB7 345 997448 HOLCOMB 115 1 | 336 | 358.5 | 0.36671 | 100.11 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03185 | 113.94 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03311 | 115.7 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03311 | 115.76 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03524 | 112.39 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03525 | 110.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.16 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.2 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.22 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.23 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.29 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.29 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.29 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.31 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.32 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.34 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.34 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.42 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.42 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.43 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.49 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.51 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.52 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.59 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.59 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.6 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.62 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.63 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.7 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.73 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.78 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.8 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.8 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.8 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.82 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.96 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 110.98 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 111 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 111.03 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 111.04 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 111.04 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 111.13 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 111.13 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 111.24 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 111.24 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03528 | 112.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0353 | 110.3 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0353 | 110.31 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0353 | 110.34 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0353 | 110.51 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0353 | 110.51 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0353 | 110.51 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0353 | 110.53 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0353 | 112.6 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03531 | 111.02 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03531 | 111.02 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03531 | 111.02 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03532 | 110.45 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03532 | 110.46 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03538 | 110.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03539 | 110.33 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03542 | 110.93 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03542 | 110.93 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03542 | 110.93 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03543 | 110.27 | 300137 4BRISTOW 138 300686 4WOODY 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03547 | 114.25 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0355 | 111.08 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0355 | 111.16 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.0355 | 111.16 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03552 | 110.53 | P23:345:WERE:WICH-345-116:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03553 | 111.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03566 | 111.14 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03611 | 112.85 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03667 | 113.88 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03741 | 117.46 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03741 | 117.51 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03741 | 117.51 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03741 | 117.51 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03753 | 117.76 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03819 | 120.04 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03829 | 116.57 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03919 | 112.93 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04587 | 114.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-177 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04587 | 114.39 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524648 CARGILL 3 115 524655 FRIONA 3 115 1 | 95.6 | 105 | 0.04356 | 110.09 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524648 CARGILL 3 115 524655 FRIONA 3 115 1 | 95.6 | 105 | 0.04356 | 110.36 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04356 | 149.04 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04356 | 149.32 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04439 | 121.26 | P12:115:SPS:T04_1_TRABLNC_CASTRO:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04471 | 113.37 | 524623 DEAFSMITH 6 230 3WXFMR SIEMT0012801 2 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04554 | 130.16 | Potential P4 Event - POI 762216_14 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04554 | 130.16 | Potential P4 Event - POI 762467_7 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04557 | 120.76 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04558 | 122.83 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04558 | 122.85 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04558 | 122.85 | Potential P4 Event - POI 774180_0 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04558 | 122.85 | Potential P4 Event - POI 774180_1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04561 | 113.4 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04562 | 114.77 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04562 | 114.77 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04562 | 114.77 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04562 | 114.86 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.42 | P12:EHV:EES::8MT_OLIVE%:LAYFLD8%:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.64 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.65 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.66 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.67 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.67 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.67 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.67 | P23:500:EES:PERVIL:R9872 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.68 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.68 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.68 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.68 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.7 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.7 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.7 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.7 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.7 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.71 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.71 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.71 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.71 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.72 | P13:SH902T GSU | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.72 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.73 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.73 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.73 | P11:024:DPC:ALMA2:6 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.73 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.73 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.76 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.77 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.8 | 640065 AXTELL 3 345 764420 GEN-2020-011 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.8 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.81 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.82 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.84 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.84 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.84 | P23:345:XEL:8H14 PRI | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.85 | P23:345:XEL:8H17 PRI AS | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.9 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.9 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.91 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.91 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.91 | P23:345:XEL:8N8 MNN | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.92 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.93 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.95 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.95 | P23:345:MEC:CBEC 908 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.97 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 111.97 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112 | P23:345:MEC:CBEC 905 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112.03 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112.04 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112.07 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112.08 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112.08 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112.16 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112.16 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 112.25 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 113.22 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 113.38 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 113.38 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 113.51 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 113.63 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 113.63 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 115.04 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 115.27 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 116.57 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04563 | 117.17 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04569 | 120.39 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04584 | 118.75 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04584 | 118.75 | Potential P4 Event - POI 525832_5 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 93.2 | 102.6 | 0.04584 | 118.75 | Potential P4 Event - POI 525832_7 | TDF Impact | Curry - Deafsmith 115 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524822 CURRY 3 115 524908 ROOSEVELT 3 115 2 | 158 | 174 | 0.06317 | 106.02 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 319 | 319 | 0.12423 | 107.18 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-178 | FROM->TO | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 319 | 319 | 0.12715 | 108.58 | 524770 PLSNT_HILL 6 230 524909 ROOSEVELT 6 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-180 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.1156 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-180 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.1156 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-180 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.1156 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.21989 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.21989 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.21989 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.03069 | 101.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.03069 | 101.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.03069 | 101.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.03069 | 101.62 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.03069 | 101.62 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06157 | 104.01 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06157 | 104.01 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06157 | 109.43 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06157 | 109.43 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06157 | 109.43 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06157 | 109.45 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06157 | 109.45 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.06529 | 106.73 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06157 | 111.97 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06157 | 111.97 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06157 | 117.94 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06157 | 117.94 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06157 | 117.94 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06157 | 117.97 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06157 | 117.97 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.06529 | 114.99 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 135.18 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 135.18 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 139.59 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 139.59 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 139.6 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 139.62 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 139.62 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03366 | 136.74 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06157 | 121.82 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06157 | 121.82 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06157 | 127.38 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06157 | 127.38 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06157 | 127.39 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06157 | 127.4 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06157 | 127.4 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.06529 | 124.55 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03098 | 133.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 115.48 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 115.6 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 115.6 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 118.12 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 118.58 | Potential P4 Event - POI 764115_0 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 118.6 | Potential P4 Event - POI 764115_2 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 128.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04419 | 143.96 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03002 | 101.47 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03018 | 101.28 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0303 | 102.03 | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.0303 | 102.34 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.03958 | 108.03 | P12:345:OKGE-AEPW:BKRBKR365:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04111 | 122.73 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04111 | 125.37 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04111 | 125.37 | Potential P4 Event - POI 514801_4 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04111 | 125.38 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04111 | 125.43 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04111 | 125.43 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04308 | 124.73 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04801 | 112.55 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04801 | 112.91 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04801 | 112.91 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04801 | 115.34 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04801 | 116.77 | Potential P4 Event - POI 764115_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04801 | 116.78 | Potential P4 Event - POI 764115_2 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.04801 | 126.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.06023 | 134.08 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03098 | 129.35 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 111.82 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 111.93 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 111.93 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 114.45 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 114.9 | Potential P4 Event - POI 764115_0 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 114.92 | Potential P4 Event - POI 764115_2 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03202 | 125.1 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04419 | 140.31 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03098 | 124.59 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03202 | 107.21 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03202 | 107.32 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03202 | 107.32 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03202 | 109.83 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03202 | 110.28 | Potential P4 Event - POI 764115_0 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03202 | 110.3 | Potential P4 Event - POI 764115_2 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03202 | 120.45 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04419 | 135.7 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.17533 | 102.19 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.17533 | 101.74 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 154.69 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 154.69 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 159.21 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 159.21 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 159.23 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 159.25 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03249 | 159.25 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.03366 | 156.31 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04111 | 113.47 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04111 | 115.9 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04111 | 115.9 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04111 | 115.9 | Potential P4 Event - POI 514801_3 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04111 | 115.95 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04111 | 115.95 | Potential P4 Event - POI 514801_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04308 | 115.31 | Potential P4 Event - POI 515800_14 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04801 | 104.12 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04801 | 104.44 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04801 | 104.44 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04801 | 106.68 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04801 | 108 | Potential P4 Event - POI 764115_1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04801 | 108.01 | Potential P4 Event - POI 764115_2 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04801 | 116.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06023 | 124.02 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06157 | 109.11 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06157 | 109.11 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06157 | 114.58 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06157 | 114.58 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06157 | 114.59 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06157 | 114.6 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06157 | 114.6 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.06529 | 111.84 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3344 | 111.08 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33443 | 111.16 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33443 | 111.16 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33469 | 110.93 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33469 | 110.93 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33469 | 110.93 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3352 | 110.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33569 | 110.53 | P23:345:WERE:WICH-345-116:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33584 | 110.45 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33584 | 110.46 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33594 | 110.33 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.336 | 110.3 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.336 | 110.31 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33604 | 110.53 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33605 | 110.34 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33607 | 110.51 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33607 | 110.51 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33607 | 110.51 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33607 | 112.6 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33617 | 110.27 | 300137 4BRISTOW 138 300686 4WOODY 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.16 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.2 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.22 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.23 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.29 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.29 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.29 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.31 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.32 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.34 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.34 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.42 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.42 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.43 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.49 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.51 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.52 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.59 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.59 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.6 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.62 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.63 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.7 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.73 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.78 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.8 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.8 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.8 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.82 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.96 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 110.98 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 111 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 111.03 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 111.04 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 111.04 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 111.13 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 111.13 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 111.24 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 111.24 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33619 | 112.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33663 | 110.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33668 | 111.02 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33668 | 111.02 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33668 | 111.02 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33809 | 112.39 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.33947 | 111.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34058 | 112.85 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3411 | 114.25 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34133 | 111.14 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34283 | 113.94 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34346 | 113.88 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3454 | 115.7 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.3454 | 115.76 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.34552 | 112.93 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35043 | 117.46 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35043 | 117.51 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35043 | 117.51 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35043 | 117.51 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35057 | 117.76 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35521 | 120.04 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35852 | 114.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.35852 | 114.39 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.359 | 116.57 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50747 | 132.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50747 | 132.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50747 | 132.22 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50747 | 132.22 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50747 | 135.65 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50747 | 135.66 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50747 | 135.69 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50747 | 135.71 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50747 | 149.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.50747 | 109.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03344 | 105.2 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03344 | 105.41 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03344 | 105.41 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03344 | 105.97 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03344 | 105.98 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03344 | 106.79 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03344 | 106.79 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.43993 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.43993 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.43993 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.43993 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.43993 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.43993 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.44546 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.45624 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 103.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 103.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 110.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 110.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 110.6 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 110.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.18366 | 112.3 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.18366 | 112.3 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 103.44 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 103.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 110.17 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 110.17 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 110.17 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.15521 | 110.18 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.18366 | 112.61 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.18366 | 112.61 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03537 | 139.27 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03932 | 139.27 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03932 | 143.74 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03932 | 143.76 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03932 | 143.76 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03932 | 143.76 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.03932 | 143.77 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.04179 | 141.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03537 | 143.04 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03932 | 143.04 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03932 | 147.51 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03932 | 147.53 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03932 | 147.53 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03932 | 147.53 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.03932 | 147.54 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.04179 | 145.38 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03537 | 135.75 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03932 | 135.75 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03932 | 140.2 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03932 | 140.22 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03932 | 140.22 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03932 | 140.22 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03932 | 140.23 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04179 | 138.07 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05091 | 102.72 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05091 | 102.72 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05091 | 106.43 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05091 | 106.43 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05091 | 106.43 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05091 | 106.43 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05091 | 106.45 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.05361 | 104.53 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05091 | 110.29 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05091 | 110.29 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05091 | 114.03 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05091 | 114.04 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05091 | 114.04 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05091 | 114.04 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05091 | 114.05 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.05361 | 112.1 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04711 | 119.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04711 | 119.34 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04711 | 123.23 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04711 | 123.23 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04711 | 123.24 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04711 | 123.24 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04711 | 123.24 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04887 | 121.01 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04896 | 102.72 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04896 | 102.73 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.04896 | 111.27 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04711 | 116.8 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04711 | 116.8 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04711 | 120.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04711 | 120.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04711 | 120.69 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04711 | 120.69 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04711 | 120.69 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04887 | 118.46 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04896 | 100.22 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04896 | 100.23 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.04896 | 108.76 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05091 | 118.22 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05091 | 118.22 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05091 | 122 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05091 | 122 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05091 | 122 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05091 | 122 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05091 | 122.01 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.05361 | 120.05 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 116.33 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 116.33 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 120.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 120.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 120.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 120.11 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 120.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05361 | 118.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 116.33 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 116.33 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 120.1 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 120.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 120.1 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 120.1 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05091 | 120.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.05361 | 118.15 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03053 | 116.3 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.031 | 110.14 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03119 | 102.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03119 | 104.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03186 | 106.31 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03186 | 106.85 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03186 | 106.85 | Potential P4 Event - POI 514801_3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03186 | 106.88 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03298 | 112.66 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03298 | 112.69 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03298 | 112.69 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 490 | 540 | 0.03298 | 112.69 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.12359 | 100.9 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.12359 | 105.66 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.12334 | 119.99 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 532937 NEOSHO 5 161 997363 NEOSHO TX-5 138 1 | 150 | 165 | 0.23293 | 109.71 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 532937 NEOSHO 5 161 997364 NEOSHO TX-4 138 1 | 112 | 123.2 | 0.17042 | 107.11 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 533020 NEOSHOS4 138 997363 NEOSHO TX-5 138 1 | 150 | 165 | 0.23293 | 109.48 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 533021 NEOSHO 4 138 997364 NEOSHO TX-4 138 1 | 112 | 123.2 | 0.17042 | 106.88 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 533758 CRAWFOR2 69.0 533772 SE1GREE2 69.0 1 | 48 | 57 | 0.04485 | 117.41 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 533762 GIR JCT2 69.0 533772 SE1GREE2 69.0 1 | 55 | 57 | 0.04485 | 110.66 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.54893 | 105.21 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.84937 | 107.71 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.84937 | 110.76 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.84937 | 110.76 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.06 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.07 | 655849 VEEDER -MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.08 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.08 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.08 | P13:069-161:OPPD:S1217 T1:LT::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.08 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.09 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.09 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.12 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.14 | P12:345:XEL:ASAK-ECL SPS | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.15 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.16 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.16 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.19 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.24 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.35 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.39 | P13:230:EES:NINEMI:AT4 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.41 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.49 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.5 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.53 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.73 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.76 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.82 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.84 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.89 | P11:HV:EES::1ISES U1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.93 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 104.93 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 105.46 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 105.51 | P13:161-22:AEPW:FLINTCR5:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 105.83 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 106.19 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 106.19 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 107.23 | 547498 STL439 5 161 547655 S1G439 1 13.2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 107.3 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 107.3 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85226 | 107.3 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85227 | 104.06 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85227 | 104.11 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85227 | 104.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85227 | 104.16 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85227 | 104.16 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85227 | 104.19 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85227 | 104.28 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85227 | 104.29 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85227 | 104.3 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85227 | 104.37 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85228 | 104.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85229 | 104.95 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8523 | 104.29 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85231 | 104.09 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85232 | 105.68 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85232 | 105.69 | P23:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85234 | 104.73 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85239 | 106.14 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85243 | 106.92 | P42:345:OKGE:SB_RARD7313:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85243 | 107.11 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85244 | 105.16 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85244 | 105.31 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85244 | 107.45 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85244 | 107.45 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85245 | 107.91 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85247 | 105.48 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85247 | 105.48 | P21:161:EES-EAI:HRSN_E:EVRTON:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85247 | 105.54 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85247 | 105.55 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85247 | 105.55 | P21:161:EES-EAI:ST_JOE_E:HILTOP_E:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85247 | 105.98 | P12:HV:EES::5HILLTOP%:NORFORK5!:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85247 | 107.08 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85247 | 108.16 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85251 | 108.91 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85252 | 105.27 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85266 | 105.03 | P23:345:AEPW:NES CB 3417B NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85266 | 105.03 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85278 | 106.83 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85283 | 105.35 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85298 | 105.69 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85303 | 108.62 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85309 | 108.7 | Potential P4 Event - POI 774740_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85309 | 108.7 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85371 | 105.69 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85384 | 105.45 | P12:69:WERE:FRAN-NSES-69:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85456 | 112.05 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85456 | 112.07 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85491 | 110.97 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85496 | 111.3 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85496 | 111.3 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8551 | 114.33 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8568 | 107.02 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8568 | 107.05 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85681 | 108.65 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85688 | 119.48 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.86053 | 125.69 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.86053 | 125.7 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.86296 | 125.92 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-195 | FROM->TO | 524822 CURRY 3 115 524908 ROOSEVELT 3 115 2 | 158 | 174 | 0.03239 | 106.02 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-195 | FROM->TO | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 319 | 319 | 0.06368 | 107.18 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-195 | FROM->TO | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 319 | 319 | 0.06521 | 108.58 | 524770 PLSNT_HILL 6 230 524909 ROOSEVELT 6 230 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-199 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05375 | 111.04 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-199 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.05375 | 111.04 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-199 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-199 | FROM->TO | 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | 120 | 120 | 0.03362 | 103.25 | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-199 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-201 | FROM->TO | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 | 478 | 478 | 0.06419 | 103.69 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | TDF Impact | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-201 | FROM->TO | 527894 HOBBS_INT 6 230 997499 HICO 68759-1 230 1 | 528 | 607 | 0.20605 | 102.31 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | TDF Impact | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-201 | FROM->TO | 527896 HOBBS_INT 7 345 997499 HICO 68759-1 230 1 | 528 | 607 | 0.20605 | 103.84 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | TDF Impact | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-203 | FROM->TO | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 | 478 | 478 | 0.12566 | 103.69 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | TDF Impact | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-205 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.20403 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-205 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.20403 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-205 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.20403 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-205 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.16113 | 100.31 | 510898 OKMULGE4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-205 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.16113 | 105.31 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-205 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.16113 | 111.62 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-209 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 | 318.7 | 318.7 | 0.03075 | 100.58 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.04883 | 100.31 | 510898 OKMULGE4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.04883 | 105.31 | 510892 HENRYET4 138 510931 KELCO 4 138 1 | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.04883 | 111.62 | P12:138:AEPW:HENRYET4:WELETK4::: | TDF Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.08145 | 102.19 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.08145 | 101.74 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.21161 | 112.3 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.21161 | 112.3 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 103.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 103.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 110.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 110.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 110.6 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 110.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.21161 | 112.61 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.21161 | 112.61 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 103.44 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 103.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 110.17 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 110.17 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 110.17 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.22437 | 110.18 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03274 | 107.91 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03318 | 106.92 | P42:345:OKGE:SB_RARD7313:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03318 | 107.11 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03347 | 107.45 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03347 | 107.45 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.39669 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.39669 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.39669 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-212 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.03443 | 111.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-213 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.16174 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-213 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.16174 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-213 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.16174 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.0388 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04076 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04078 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04078 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04078 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04078 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04078 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-213 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.04078 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-216 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.0506 | 111.04 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-216 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.0506 | 111.04 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-216 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-216 | FROM->TO | 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | 120 | 120 | 0.03244 | 103.25 | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-216 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-217 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.0506 | 111.04 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-217 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.0506 | 111.04 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-217 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-217 | FROM->TO | 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | 120 | 120 | 0.03244 | 103.25 | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-217 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-218 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.0506 | 111.04 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-218 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.0506 | 111.04 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-218 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-218 | FROM->TO | 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | 120 | 120 | 0.03244 | 103.25 | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-218 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-219 | FROM->TO | 533301 EAST ST3 115 533309 WEMPORI3 115 1 | 92 | 92 | 0.10222 | 100.23 | 533307 PRAIRIE3 115 533309 WEMPORI3 115 1 | TDF Impact | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-219 | FROM->TO | 533301 EAST ST3 115 533309 WEMPORI3 115 1 | 92 | 92 | 0.10222 | 103.09 | P12:115:WERE:LANG-WEMP-115:::HV: | TDF Impact | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-219 | FROM->TO | 533301 EAST ST3 115 533309 WEMPORI3 115 1 | 92 | 92 | 0.10222 | 110.31 | 533304 LANG 3 115 533307 PRAIRIE3 115 1 | TDF Impact | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.0554 | 111.04 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.0554 | 111.04 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.26483 | 117.89 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.26596 | 118.39 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.15976 | 126.72 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.15976 | 129.35 | P12:115:SUNC:CONCORDIA-CLIFTON:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16749 | 134.15 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16784 | 120.67 | P12:115:HAST:::LINE 1159B EGYCNTR7 - SUTTON 7:HV:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.169 | 122.44 | 533163 HOYT 3 115 533165 HTI JCT3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16925 | 124.27 | P23:345:WERE:SUMM-345-218:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16936 | 123.6 | 539805 ELMCREEK7 345 3WXFMR ELMCREEK T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16936 | 123.6 | 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16936 | 123.61 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16936 | 126.2 | Potential P4 Event - POI 532773_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1701 | 118.88 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1701 | 119.03 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1701 | 119.1 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1701 | 122.19 | Potential P4 Event - POI 515576_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.68 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.8 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.84 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.89 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.9 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.9 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.95 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.95 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.96 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.96 | P13:138:EES:LC:T2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.97 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.09 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.1 | 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.1 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.12 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.14 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.18 | 508286 CAMPCOR4 138 765980 GEN-2021-075 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.18 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.2 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.2 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.24 | 526936 YOAKUM 7 345 763516 GEN-2019-011 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.28 | 512749 PAWNSW4 138 773121 GEN-2023-057 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.35 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.45 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.52 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.55 | P13:230:EES:NINEMI:AT4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.58 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.61 | 511477 S.W.S.-4 138 776561 GEN-2023-229 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.62 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.62 | P13:345:GRDA:GRDA2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.63 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.64 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.64 | P12:161:GRDA:SALINA 5-SALNCRK5:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.65 | P11:16:EES-EAI:MAGNET:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.65 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.67 | 508298 LYDIA 7 345 764075 GEN-2020-054 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.73 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.82 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.85 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.87 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.24 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.34 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.48 | 776401 GEN-2023-221 345 776402 G23-221XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.5 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.61 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.66 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.72 | 525481 PLANT_X 6 230 774821 GEN-2023-142 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.72 | P12:EHV:EES::8ANO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.84 | P11:25:EES:WATERF:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.84 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.85 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.94 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.98 | 766260 GEN-2020-007 345 766261 G20-007-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.05 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.05 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.15 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.15 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.5 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.57 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.58 | GEN-2023-102_POI_515852_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.79 | Potential P4 Event - POI 515576_20 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 122.21 | GEN-2021-005_POI_532773_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 122.22 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 122.24 | Potential P4 Event - POI 337561_27 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 122.98 | 640218 HEBRN N7 115 640012 HEBRON G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 123.56 | Potential P4 Event - POI 515852_14 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 124.55 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17012 | 125.4 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17013 | 120.32 | P42:500:OKGE:SB_FTTH8581:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17013 | 120.32 | P42:500:OKGE:SB_FTTH8585:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17013 | 120.35 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17015 | 119.28 | 635580 ARBOR HILL 3 345 635622 RCCN TRL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17016 | 119.01 | P23:345:MEC:BOONEVILLE:901:_1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17045 | 120.23 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17045 | 120.23 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17045 | 120.23 | P45:345:OPPD:S3454-S3455&WAG:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17064 | 119.27 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1736 | 124.62 | Potential P4 Event - POI 640271_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19659 | 130.97 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19659 | 132.82 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23306 | 161.23 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23306 | 161.48 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26581 | 183.63 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.30493 | 156.37 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 156.73 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 156.79 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 154.8 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31466 | 157.42 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31468 | 154.88 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31472 | 155.53 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31472 | 155.54 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31475 | 155.39 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31475 | 155.42 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31479 | 154.45 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31479 | 154.5 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3148 | 154.84 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3148 | 154.84 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.19 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.19 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.43 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.52 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.71 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.94 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 156.14 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 153.83 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 153.86 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 153.87 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 153.88 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.1 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.13 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.14 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.14 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.14 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.14 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.16 | 514876 SW134TP4 138 514928 SOGATE 4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.16 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.17 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.19 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.2 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.22 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.22 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.22 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.25 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.31 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.31 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.31 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.31 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.32 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.34 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.38 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.41 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.44 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.45 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.5 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.5 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.57 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.59 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.6 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.62 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.62 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.67 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.71 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.75 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.75 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.88 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.89 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.01 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.03 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.24 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.27 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.34 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.34 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.34 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.62 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.72 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.93 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.94 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 156.01 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 156.04 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 156.16 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 156.4 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 157.19 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 157.91 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 160.58 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31488 | 154.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31488 | 154.46 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31489 | 154.15 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31489 | 154.32 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31489 | 154.37 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31498 | 156.15 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31525 | 155.12 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31542 | 155.86 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31542 | 155.92 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31542 | 156.7 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31581 | 155.26 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32259 | 157.41 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.33067 | 158.13 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3425 | 169.86 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3425 | 170.16 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.35044 | 166.06 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37543 | 183.54 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55985 | 273.17 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 146.56 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 146.63 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 144.72 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4063 | 146.15 | Potential P4 Event - POI 640590_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40671 | 147.23 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40674 | 144.8 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4068 | 145.42 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4068 | 145.43 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40683 | 145.29 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40684 | 145.31 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40689 | 144.39 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40689 | 144.43 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4069 | 144.76 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4069 | 144.76 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40693 | 146 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.14 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.14 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.37 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.46 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.64 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.86 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 143.11 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 143.79 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 143.83 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 143.83 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.05 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.08 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.09 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.09 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.09 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.09 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.11 | 514876 SW134TP4 138 514928 SOGATE 4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.11 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.12 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.14 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.14 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.16 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.16 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.17 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.2 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.25 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.25 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.25 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.25 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.26 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.32 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.35 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.38 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.39 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.44 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.44 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.5 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.53 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.53 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.55 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.55 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.6 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.64 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.68 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.68 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.8 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.8 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.81 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.92 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.94 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.14 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.17 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.23 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.51 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.6 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.8 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.91 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 146.03 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 146.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 147.01 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 147.7 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 150.26 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40696 | 144.29 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.407 | 144.14 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.407 | 144.4 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40701 | 144.1 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40701 | 144.32 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40702 | 144.26 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40714 | 146.01 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40748 | 145.03 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4077 | 145.74 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4077 | 145.79 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4077 | 146.55 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40821 | 145.17 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41696 | 147.22 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42741 | 147.91 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45297 | 155.51 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48527 | 172.25 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61527 | 214.75 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61527 | 217.85 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61527 | 218.14 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 174.27 | P11:14:NPPD:BPS GT2G:2:90:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 174.28 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 174.29 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 2 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 153.46 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 153.53 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 151.5 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31433 | 153.03 | Potential P4 Event - POI 640590_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31466 | 154.19 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31468 | 151.59 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31472 | 152.25 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31472 | 152.27 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31475 | 152.11 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31475 | 152.14 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31479 | 151.15 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31479 | 151.2 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3148 | 151.55 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3148 | 151.55 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 150.89 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 150.89 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 151.13 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 151.23 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 151.42 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 151.65 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 152.88 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.56 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.56 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.57 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.79 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.82 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.83 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.84 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.84 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.84 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.85 | 514876 SW134TP4 138 514928 SOGATE 4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.86 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.87 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.89 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.89 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.91 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.91 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.92 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.95 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.01 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.01 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.01 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.01 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.02 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.04 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.08 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.11 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.15 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.15 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.2 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.2 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.27 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.3 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.3 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.33 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.33 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.38 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.42 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.46 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.46 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.59 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.6 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.6 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.72 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.75 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.95 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.99 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.07 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.07 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.35 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.66 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.74 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.77 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.9 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 153.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 153.95 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 154.68 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 157.42 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31488 | 150.89 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31488 | 151.17 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31489 | 150.85 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31489 | 151.02 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31489 | 151.08 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31498 | 152.89 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31525 | 151.83 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31542 | 152.59 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31542 | 152.65 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31542 | 153.46 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31581 | 151.98 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32259 | 154.17 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.33067 | 154.91 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3425 | 166.89 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3425 | 167.19 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.35044 | 163.02 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37543 | 180.85 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55985 | 272.34 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13516 | 106.17 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13516 | 106.2 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.15429 | 119.44 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | 120 | 120 | 0.03546 | 103.25 | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 2 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.0554 | 111.04 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 229 | 229 | 0.0554 | 111.04 | Potential P4 Event - POI 640065_3 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.26483 | 117.89 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.26596 | 118.39 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.15976 | 126.72 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.15976 | 129.35 | P12:115:SUNC:CONCORDIA-CLIFTON:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16749 | 134.15 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16784 | 120.67 | P12:115:HAST:::LINE 1159B EGYCNTR7 - SUTTON 7:HV:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.169 | 122.44 | 533163 HOYT 3 115 533165 HTI JCT3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16925 | 124.27 | P23:345:WERE:SUMM-345-218:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16936 | 123.6 | 539805 ELMCREEK7 345 3WXFMR ELMCREEK T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16936 | 123.6 | 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16936 | 123.61 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16936 | 126.2 | Potential P4 Event - POI 532773_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1701 | 118.88 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1701 | 119.03 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1701 | 119.1 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1701 | 122.19 | Potential P4 Event - POI 515576_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.68 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.8 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.84 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.89 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.9 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.9 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.95 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.95 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.96 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.96 | P13:138:EES:LC:T2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 118.97 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.09 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.1 | 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.1 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.12 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.14 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.18 | 508286 CAMPCOR4 138 765980 GEN-2021-075 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.18 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.2 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.2 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.24 | 526936 YOAKUM 7 345 763516 GEN-2019-011 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.28 | 512749 PAWNSW4 138 773121 GEN-2023-057 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.35 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.45 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.52 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.55 | P13:230:EES:NINEMI:AT4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.58 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.61 | 511477 S.W.S.-4 138 776561 GEN-2023-229 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.62 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.62 | P13:345:GRDA:GRDA2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.63 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.64 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.64 | P12:161:GRDA:SALINA 5-SALNCRK5:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.65 | P11:16:EES-EAI:MAGNET:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.65 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.67 | 508298 LYDIA 7 345 764075 GEN-2020-054 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.73 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.82 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.85 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 119.87 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.24 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.34 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.48 | 776401 GEN-2023-221 345 776402 G23-221XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.5 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.61 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.66 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.72 | 525481 PLANT_X 6 230 774821 GEN-2023-142 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.72 | P12:EHV:EES::8ANO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.84 | P11:25:EES:WATERF:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.84 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.85 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.94 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 120.98 | 766260 GEN-2020-007 345 766261 G20-007-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.05 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.05 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.15 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.15 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.5 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.57 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.58 | GEN-2023-102_POI_515852_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 121.79 | Potential P4 Event - POI 515576_20 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 122.21 | GEN-2021-005_POI_532773_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 122.22 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 122.24 | Potential P4 Event - POI 337561_27 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 122.98 | 640218 HEBRN N7 115 640012 HEBRON G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 123.56 | Potential P4 Event - POI 515852_14 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17011 | 124.55 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17012 | 125.4 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17013 | 120.32 | P42:500:OKGE:SB_FTTH8581:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17013 | 120.32 | P42:500:OKGE:SB_FTTH8585:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17013 | 120.35 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17015 | 119.28 | 635580 ARBOR HILL 3 345 635622 RCCN TRL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17016 | 119.01 | P23:345:MEC:BOONEVILLE:901:_1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17045 | 120.23 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17045 | 120.23 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17045 | 120.23 | P45:345:OPPD:S3454-S3455&WAG:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17064 | 119.27 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1736 | 124.62 | Potential P4 Event - POI 640271_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19659 | 130.97 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19659 | 132.82 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23306 | 161.23 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23306 | 161.48 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26581 | 183.63 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.30493 | 156.37 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 156.73 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 156.79 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 154.8 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31466 | 157.42 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31468 | 154.88 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31472 | 155.53 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31472 | 155.54 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31475 | 155.39 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31475 | 155.42 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31479 | 154.45 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31479 | 154.5 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3148 | 154.84 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3148 | 154.84 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.19 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.19 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.43 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.52 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.71 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 154.94 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31483 | 156.14 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 153.83 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 153.86 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 153.87 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 153.88 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.1 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.13 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.14 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.14 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.14 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.14 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.16 | 514876 SW134TP4 138 514928 SOGATE 4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.16 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.17 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.19 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.2 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.22 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.22 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.22 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.25 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.31 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.31 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.31 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.31 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.32 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.34 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.38 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.41 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.44 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.45 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.5 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.5 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.57 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.59 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.6 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.62 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.62 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.67 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.71 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.75 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.75 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.88 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.89 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 154.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.01 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.03 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.24 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.27 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.34 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.34 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.34 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.62 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.72 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.93 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 155.94 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 156.01 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 156.04 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 156.16 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 156.4 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 157.19 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 157.91 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31484 | 160.58 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31488 | 154.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31488 | 154.46 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31489 | 154.15 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31489 | 154.32 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31489 | 154.37 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31498 | 156.15 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31525 | 155.12 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31542 | 155.86 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31542 | 155.92 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31542 | 156.7 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31581 | 155.26 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32259 | 157.41 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.33067 | 158.13 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3425 | 169.86 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3425 | 170.16 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.35044 | 166.06 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37543 | 183.54 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55985 | 273.17 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 146.56 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 146.63 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 144.72 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4063 | 146.15 | Potential P4 Event - POI 640590_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40671 | 147.23 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40674 | 144.8 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4068 | 145.42 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4068 | 145.43 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40683 | 145.29 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40684 | 145.31 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40689 | 144.39 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40689 | 144.43 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4069 | 144.76 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4069 | 144.76 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40693 | 146 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.14 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.14 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.37 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.46 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.64 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40694 | 144.86 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 143.11 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 143.79 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 143.83 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 143.83 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.05 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.08 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.09 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.09 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.09 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.09 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.11 | 514876 SW134TP4 138 514928 SOGATE 4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.11 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.12 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.14 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.14 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.16 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.16 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.17 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.2 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.25 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.25 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.25 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.25 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.26 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.32 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.35 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.38 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.39 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.44 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.44 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.5 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.53 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.53 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.55 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.55 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.6 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.64 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.68 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.68 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.8 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.8 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.81 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.92 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 144.94 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.14 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.17 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.23 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.51 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.6 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.8 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 145.91 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 146.03 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 146.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 147.01 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 147.7 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40695 | 150.26 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40696 | 144.29 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.407 | 144.14 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.407 | 144.4 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40701 | 144.1 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40701 | 144.32 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40702 | 144.26 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40714 | 146.01 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40748 | 145.03 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4077 | 145.74 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4077 | 145.79 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4077 | 146.55 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40821 | 145.17 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41696 | 147.22 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42741 | 147.91 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45297 | 155.51 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48527 | 172.25 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61527 | 214.75 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61527 | 217.85 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61527 | 218.14 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 174.27 | P11:14:NPPD:BPS GT2G:2:90:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 174.28 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 174.29 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 153.46 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 153.53 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 151.5 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31433 | 153.03 | Potential P4 Event - POI 640590_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31466 | 154.19 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31468 | 151.59 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31472 | 152.25 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31472 | 152.27 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31475 | 152.11 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31475 | 152.14 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31479 | 151.15 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31479 | 151.2 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3148 | 151.55 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3148 | 151.55 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 150.89 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 150.89 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 151.13 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 151.23 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 151.42 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 151.65 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31483 | 152.88 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.56 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.56 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.57 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.79 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.82 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.83 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.84 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.84 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.84 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.85 | 514876 SW134TP4 138 514928 SOGATE 4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.86 | P12:345:AMMO::MAYWOOD:SUBT:77 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.87 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.89 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.89 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.91 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.91 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.92 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 150.95 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.01 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.01 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.01 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.01 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.02 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.04 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.08 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.11 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.15 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.15 | 763439 GEN-2018-131 345 763443 G18-131-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.2 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.2 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.27 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.3 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.3 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.33 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.33 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.38 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.42 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.46 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.46 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.59 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.6 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.6 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.72 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.75 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.95 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 151.99 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.07 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.07 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.35 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.66 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.74 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.77 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 152.9 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 153.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 153.95 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 154.68 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31484 | 157.42 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31488 | 150.89 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31488 | 151.17 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31489 | 150.85 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31489 | 151.02 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31489 | 151.08 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31498 | 152.89 | Potential P4 Event - POI 640065_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31525 | 151.83 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31542 | 152.59 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31542 | 152.65 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31542 | 153.46 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31581 | 151.98 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32259 | 154.17 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.33067 | 154.91 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3425 | 166.89 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3425 | 167.19 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.35044 | 163.02 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37543 | 180.85 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55985 | 272.34 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13516 | 106.17 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13516 | 106.2 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.15429 | 119.44 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | 120 | 120 | 0.03546 | 103.25 | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | TDF Impact | Build new AXTELL 7 to KEARNEY7 115kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 484 | 515 | 0.07757 | 102.19 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 484 | 515 | 0.07757 | 101.74 | Potential P4 Event - POI 515800_5 | TDF Impact | Gracemont to Treasure Island 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09897 | 120.04 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09921 | 117.76 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.09982 | 113.88 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1091 | 117.46 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1091 | 117.51 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1091 | 117.51 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.1091 | 117.51 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11029 | 112.85 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11537 | 114.25 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11647 | 112.39 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11742 | 111.02 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11742 | 111.02 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11742 | 111.02 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11788 | 110.53 | P23:345:WERE:WICH-345-116:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11801 | 110.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11818 | 111.08 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11818 | 111.16 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11818 | 111.16 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.16 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.2 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.22 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.23 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.29 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.29 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.29 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.31 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.32 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.34 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.34 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.42 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.42 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.43 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.49 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.51 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.52 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.59 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.59 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.6 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.62 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.63 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.7 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.73 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.78 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.8 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.8 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.8 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.82 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.96 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 110.98 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 111 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 111.03 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 111.04 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 111.04 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 111.13 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 111.13 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 111.24 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 111.24 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 112.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11823 | 112.6 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11824 | 110.3 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11824 | 110.31 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11824 | 110.51 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11824 | 110.51 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11824 | 110.51 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11824 | 110.53 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11825 | 110.34 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11825 | 110.45 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11825 | 110.46 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11828 | 110.27 | 300137 4BRISTOW 138 300686 4WOODY 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11829 | 110.33 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11829 | 110.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11831 | 110.93 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11831 | 110.93 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11831 | 110.93 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11837 | 111.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11845 | 111.14 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.11962 | 113.94 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.12067 | 115.7 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.12067 | 115.76 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.12211 | 112.93 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.12363 | 114.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.12363 | 114.39 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.12447 | 116.57 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15322 | 132.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15322 | 132.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15322 | 132.22 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15322 | 132.22 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15322 | 135.65 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15322 | 135.66 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15322 | 135.69 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15322 | 135.71 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.15322 | 149.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.15322 | 109.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10623 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10623 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10623 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10623 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10623 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10623 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.10948 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.1232 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 103.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 103.34 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 110.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 110.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 110.6 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 110.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.08046 | 112.3 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.08046 | 112.3 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 103.44 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 103.44 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 110.17 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 110.17 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 110.17 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.05088 | 110.18 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.08046 | 112.61 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.08046 | 112.61 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.21507 | 101.04 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.21507 | 101.04 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.21507 | 101.04 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.0958 | 101.6 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.0958 | 101.6 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.0958 | 101.61 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.0958 | 101.62 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 212 | 212 | 0.0958 | 101.62 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11083 | 104.01 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11083 | 104.01 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11083 | 109.43 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11083 | 109.43 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11083 | 109.43 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11083 | 109.45 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11083 | 109.45 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.11274 | 106.73 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11083 | 111.97 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11083 | 111.97 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11083 | 117.94 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11083 | 117.94 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11083 | 117.94 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11083 | 117.97 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11083 | 117.97 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.11274 | 114.99 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0859 | 103.32 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09456 | 100.96 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09456 | 100.96 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09456 | 103.59 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09456 | 103.61 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09456 | 110.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09799 | 115.17 | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09799 | 116.23 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 135.18 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 135.18 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 139.59 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 139.59 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 139.6 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 139.62 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 139.62 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.102 | 136.74 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.11222 | 117.26 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.11222 | 119.07 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.11222 | 120.23 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11083 | 121.82 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11083 | 121.82 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11083 | 127.38 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11083 | 127.38 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11083 | 127.39 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11083 | 127.4 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11083 | 127.4 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 212 | 212 | 0.11274 | 124.55 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08402 | 117.31 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08466 | 114.01 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0859 | 121.97 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08739 | 108.37 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08739 | 108.4 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08739 | 108.4 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08748 | 107.9 | P12:138:OKGE-WFEC:BKRBKR368_1:27S_32S::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08748 | 107.9 | P12:138:WFEC:ANADRKO_GRCMNT_2:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08752 | 107.75 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08752 | 107.75 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.49 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.51 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.74 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.75 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.76 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.77 | P13:230:EES:NINEMI:AT4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.78 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.78 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.78 | P13:230:EES:NINEMI:AT5 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.79 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.79 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.79 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.81 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.81 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.82 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.84 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.89 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.89 | P11:HV:EES::1ISES U1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.9 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.91 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.91 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.91 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.94 | P11:25:EES:WATERF:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.94 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 107.94 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 108.24 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 108.26 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 108.34 | 775520 G23-177-TAP 138 775521 GEN-2023-177 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 108.59 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 108.63 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 108.63 | GEN-2022-238_POI_515055_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 108.76 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 108.83 | 774660 G23-134-TAP 138 774661 GEN-2023-134 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 108.83 | 774661 GEN-2023-134 138 774662 G23-134XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08754 | 108.84 | GEN-2023-134_POI_774660_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08755 | 107.88 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08755 | 108.08 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08756 | 107.74 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08757 | 107.87 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08758 | 107.92 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08758 | 107.92 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08758 | 108.21 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08758 | 108.22 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08759 | 107.85 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08759 | 108.2 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08761 | 107.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08765 | 109.04 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08767 | 108.82 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08776 | 110.21 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08777 | 109.27 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08808 | 109.42 | P12:138:OKGE:BKRBKR95:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09144 | 115.26 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09456 | 119.94 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09456 | 119.94 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09456 | 122.63 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09456 | 122.66 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09456 | 129.53 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09799 | 133.99 | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.09799 | 135.07 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 154.69 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 154.69 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 159.21 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 159.21 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 159.23 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 159.25 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.1014 | 159.25 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.102 | 156.31 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.11222 | 136.12 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.11222 | 138.02 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.11222 | 139.22 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11083 | 109.11 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11083 | 109.11 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11083 | 114.58 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11083 | 114.58 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11083 | 114.59 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11083 | 114.6 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11083 | 114.6 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.11274 | 111.84 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.26747 | 114.25 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27194 | 111.08 | P23:500:EES-EAI:ARK_NU:B5106 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27197 | 111.16 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27197 | 111.16 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27227 | 110.93 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27227 | 110.93 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27227 | 110.93 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27279 | 110.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.2732 | 110.53 | P23:345:WERE:WICH-345-116:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27344 | 110.45 | P23:500:EES:NELSON:13105::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27345 | 110.46 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27352 | 110.33 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27361 | 110.3 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27361 | 110.31 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27366 | 110.53 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27367 | 110.34 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27368 | 110.51 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27368 | 110.51 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27368 | 110.51 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27368 | 112.6 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.2738 | 110.2 | P12:HV:EES::4NAVSOTA!:4PONDEROSA%:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.2738 | 110.27 | 300137 4BRISTOW 138 300686 4WOODY 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.16 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.22 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.23 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.29 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.29 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.29 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.31 | 548808 ECKLES-161 161 772701 GEN-2023-036 161 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.32 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.34 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.34 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.42 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.42 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.43 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.49 | 542965 W.GRDNR7 345 762279 GEN-2017-195 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.51 | P23:345:XEL:8H14 PRI | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.52 | P23:345:XEL:8H17 PRI AS | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.59 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.59 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.6 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.62 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.63 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.64 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.7 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.73 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.78 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.8 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.8 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.8 | P23:345:MEC:CBEC 905 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.82 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.89 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.96 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 110.98 | 767240 G22-013-TAP 345 767241 GEN-2022-013 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 111 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 111.03 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 111.04 | 776201 GEN-2023-211 345 776202 G23-211XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 111.04 | GEN-2023-211_POI_515576_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 111.13 | 775321 GEN-2023-167 138 775322 G23-167XFMR1 34.5 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 111.13 | GEN-2023-167_POI_515156_Generator_outage | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 111.24 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 111.24 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27381 | 112.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27413 | 111.02 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27413 | 111.02 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27413 | 111.02 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27421 | 110.55 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27536 | 112.39 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27651 | 112.85 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27702 | 111.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27856 | 113.88 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.27885 | 111.14 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.2796 | 117.46 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.2796 | 117.51 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.2796 | 117.51 | Potential P4 Event - POI 774180_0 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.2796 | 117.51 | Potential P4 Event - POI 774180_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28046 | 117.76 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28212 | 120.04 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28693 | 116.57 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28974 | 114.39 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.28974 | 114.39 | P12:345:OKGE-AEPW:BKRBKR343:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.29069 | 113.94 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.29754 | 115.7 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.29754 | 115.76 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.30308 | 112.93 | P12:138:OKGE-AEPW:BKRBKR22:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.39089 | 132.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.39089 | 132.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.39089 | 132.22 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.39089 | 132.22 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.39089 | 135.65 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.39089 | 135.66 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.39089 | 135.69 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.39089 | 135.71 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.39089 | 149.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 1342 | 1541 | 0.39089 | 109.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03691 | 101.09 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03691 | 102.6 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 268 | 308 | 0.03691 | 105.49 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03691 | 111.25 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03691 | 112.75 | P12:138:OKGE:BKRBKR132:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 268 | 308 | 0.03691 | 115.66 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03455 | 106.64 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03455 | 108.22 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 382 | 382 | 0.03455 | 109.36 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03246 | 105.39 | P42:345:OKGE:SB_CION7383:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03399 | 105.2 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03399 | 105.41 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03399 | 105.41 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03399 | 105.97 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03399 | 105.98 | Potential P4 Event - POI 511568_4 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03399 | 106.79 | Potential P4 Event - POI 764115_1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03399 | 106.79 | Potential P4 Event - POI 764115_2 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03455 | 117.41 | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03455 | 118.99 | P12:138:OKGE:BKRBKR126:::: | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 382 | 382 | 0.03455 | 120.13 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Czech Hall 138 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.31249 | 108.51 | Potential P4 Event - POI 515800_16 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.31524 | 107.87 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.31524 | 111.12 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.31524 | 111.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.31524 | 111.12 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.31524 | 111.17 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.31524 | 111.17 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1058 | 1195 | 0.32362 | 110.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05044 | 101.2 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05298 | 103.38 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05298 | 103.38 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05298 | 105.84 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05298 | 105.86 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05298 | 111.67 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05477 | 107.06 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05477 | 107.08 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.05477 | 107.4 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06251 | 139.27 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06251 | 143.74 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06251 | 143.76 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06251 | 143.76 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06251 | 143.76 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06251 | 143.77 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06378 | 141.6 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06552 | 111.39 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06552 | 113.9 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06706 | 109.91 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06706 | 113.85 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 145 | 169 | 0.06824 | 139.27 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.04243 | 101.21 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05044 | 104.92 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05298 | 107.11 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05298 | 107.11 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05298 | 109.58 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05298 | 109.59 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05298 | 115.42 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05477 | 110.78 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05477 | 110.8 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.05477 | 111.12 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06251 | 143.04 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06251 | 147.51 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06251 | 147.53 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06251 | 147.53 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06251 | 147.53 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06251 | 147.54 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06378 | 145.38 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06552 | 115.12 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06552 | 117.63 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06706 | 113.61 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06706 | 117.56 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 145 | 169 | 0.06824 | 143.04 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05298 | 102.38 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05298 | 102.39 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05298 | 108.18 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05477 | 103.61 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05477 | 103.63 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.05477 | 103.95 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06251 | 135.75 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06251 | 140.2 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06251 | 140.22 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06251 | 140.22 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06251 | 140.22 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06251 | 140.23 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06378 | 138.07 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06552 | 107.93 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06552 | 110.43 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06706 | 106.46 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06706 | 110.39 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.06824 | 135.75 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08751 | 102.72 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08751 | 102.72 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08751 | 106.43 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08751 | 106.43 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08751 | 106.43 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08751 | 106.43 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.08751 | 106.45 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.0889 | 104.53 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08751 | 110.29 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08751 | 110.29 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08751 | 114.03 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08751 | 114.04 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08751 | 114.04 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08751 | 114.04 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.08751 | 114.05 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.0889 | 112.1 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08683 | 102.72 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08683 | 102.73 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08683 | 111.27 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08804 | 119.34 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08804 | 119.34 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08804 | 123.23 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08804 | 123.23 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08804 | 123.24 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08804 | 123.24 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08804 | 123.24 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.08894 | 121.01 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08683 | 100.22 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08683 | 100.23 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08683 | 108.76 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08804 | 116.8 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08804 | 116.8 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08804 | 120.68 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08804 | 120.68 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08804 | 120.69 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08804 | 120.69 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08804 | 120.69 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 145 | 169 | 0.08894 | 118.46 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08751 | 118.22 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08751 | 118.22 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08751 | 122 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08751 | 122 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08751 | 122 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08751 | 122 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.08751 | 122.01 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.0889 | 120.05 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 116.33 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 116.33 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 120.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 120.11 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 120.11 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 120.11 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 120.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0889 | 118.16 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 116.33 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 116.33 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 120.1 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 120.1 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 120.1 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 120.1 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.08751 | 120.12 | P42:345:OKGE:SB_CION7384:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-229 | FROM->TO | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 200 | 234 | 0.0889 | 118.15 | Potential P4 Event - POI 515800_14 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-236 | FROM->TO | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 | 478 | 478 | 0.08141 | 103.69 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | TDF Impact | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-236 | FROM->TO | 527894 HOBBS_INT 6 230 997499 HICO 68759-1 230 1 | 528 | 607 | 0.22261 | 102.31 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | TDF Impact | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-236 | FROM->TO | 527896 HOBBS_INT 7 345 997499 HICO 68759-1 230 1 | 528 | 607 | 0.22261 | 103.84 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | TDF Impact | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06917 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06917 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06917 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06917 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06917 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06917 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06917 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06917 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06917 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.16223 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21053 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21054 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21054 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21054 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21056 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21102 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21102 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21127 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21142 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21264 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21264 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21264 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21897 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22002 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22275 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22332 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22332 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22332 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22332 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22495 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22984 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23227 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23227 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23242 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25159 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25159 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25159 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25159 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27194 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.07277 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.07277 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.15703 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20533 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20534 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20534 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20534 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20534 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20534 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20534 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20534 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20534 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20534 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20534 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2054 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20583 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20583 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20608 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20623 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20746 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20746 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20746 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21326 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21476 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21815 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21827 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21827 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21827 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21827 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21904 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21992 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22375 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22731 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22731 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24658 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24658 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24658 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24658 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26618 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.06978 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-001 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.06978 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24895 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29727 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29731 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29765 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29765 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29785 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29799 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.3006 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30745 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30817 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30902 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31519 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31519 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31927 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.33507 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.37454 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.14184 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.14184 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.10936 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.10936 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.10936 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.19044 | 102.79 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-009 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.19044 | 102.79 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.19044 | 103.02 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-009 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.19044 | 103.02 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-012 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.03687 | 100.16 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-012 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.03687 | 100.16 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-012 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.03687 | 101.46 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-012 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.03687 | 101.57 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-012 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.04516 | 102.18 | Potential P4 Event - POI 659105_8 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-012 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.04534 | 100.55 | 659105 LELAND_O-BE3 345 659424 LO.LS-CC-BE3 345 Z | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-012 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.04534 | 100.61 | 659424 LO.LS-CC-BE3 345 764220 G20-021-TAP 345 1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-012 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.04534 | 100.61 | P12:345:UMZB:# 7129 #:: CHA IN SD. LOS - CHAPPELLE CREEK 345:EHV: | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-012 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.04534 | 100.61 | P14:345:UMZ:# 7213 #:: PROPER TAKE LINE WITH LELAND OLDS-FORT THOMPSON LINE REACTOR:EHV: | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-012 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.05266 | 107.96 | Potential P4 Event - POI 659105_15 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-012 | FROM->TO | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 239 | 239 | 0.05266 | 100.31 | Potential P4 Event - POI 659105_15 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03212 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0328 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03296 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03296 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03296 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03333 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03351 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03373 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03373 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03416 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03474 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03479 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03479 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03479 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0348 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0348 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0348 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0348 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03481 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03561 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03698 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04883 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 239 | 239 | 0.1236 | 108.04 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-015 | FROM->TO | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 195.4 | 195.4 | 0.07281 | 102.66 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-027 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.10921 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-027 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.10921 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-027 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.10921 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-028 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.38 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1041 | 104.47 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 110.44 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 111.84 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-028 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 479 | 493 | 0.03542 | 100.38 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-033 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 233 | 254 | 0.94293 | 104.54 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04217 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04217 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04217 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04217 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04217 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04217 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04217 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04217 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.04217 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05226 | 107.99 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05252 | 104.81 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05252 | 105.32 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05252 | 105.81 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05261 | 110.42 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05261 | 110.48 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05261 | 110.48 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05261 | 110.73 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05261 | 111.37 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05261 | 111.39 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05261 | 114.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05276 | 131.48 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05276 | 131.48 | Potential P4 Event - POI 515800_7 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05276 | 132.88 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05276 | 132.88 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05276 | 132.94 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05276 | 132.94 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05286 | 134.25 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.05286 | 134.25 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 29 | 35 | 0.16061 | 127.44 | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05226 | 107.6 | P12:138:WFEC:ANADRKO_PAYNE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05252 | 104.41 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05252 | 104.93 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05252 | 105.41 | 520814 ANADARK4 138 521031 POCASET4 138 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05261 | 110.03 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05261 | 110.09 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05261 | 110.09 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05261 | 110.35 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05261 | 110.99 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05261 | 111.01 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05261 | 114.23 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05276 | 131.12 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05276 | 131.12 | Potential P4 Event - POI 515800_15 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05276 | 132.53 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05276 | 132.53 | Potential P4 Event - POI 514801_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05276 | 132.59 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05276 | 132.59 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05286 | 133.9 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.05286 | 133.9 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 29 | 35 | 0.16061 | 127.01 | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 278.14 | Potential P4 Event - POI 515800_17 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 278.58 | 521089 WASHITA4 138 3WXFMR WASHITA 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 278.67 | P12:069:WFEC:ANADRKO_WASHITA:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 278.77 | 520838 CADDO 2 69.0 521088 WASHITA2 69.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 283.23 | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 288.18 | 520508 CLVJCTN2 69.0 520859 COGAR 2 69.0 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-035 | FROM->TO | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 58 | 68 | 1 | 288.18 | P12:138:WFEC:CLVLND_SCOTT:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03557 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03557 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03557 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-049 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.38 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.13554 | 104.47 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 110.44 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 111.84 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-049 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 479 | 493 | 0.0453 | 100.38 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.04101 | 122.38 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05247 | 113.33 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05252 | 112.96 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05252 | 113.02 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05254 | 115.79 | P12:161:GRDA:MIAMI 5-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05278 | 116.25 | P12:161:GRDA:PENSA 5-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05289 | 112.93 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05289 | 112.93 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05296 | 111.44 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05298 | 111.46 | P42:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05321 | 111.43 | P23:345:GMO:SIBLEY-R1-3:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05328 | 111.24 | P12:345:AMMO-GMO::OVERTON:SIBLEY:EHV | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05329 | 112.57 | P42:345:OKGE:SB_RARD7313:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05329 | 112.67 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05336 | 111.08 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05338 | 111.59 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05346 | 111.71 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05352 | 111.95 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05353 | 114.6 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05356 | 110.99 | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05393 | 110.73 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05397 | 111.19 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05397 | 111.26 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05397 | 111.28 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05426 | 110.3 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05428 | 110.45 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05429 | 110.23 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05429 | 110.23 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05431 | 110.26 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05431 | 110.38 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05433 | 110.34 | P23:345:MEC:BOONEVILLE:901:_1:: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05434 | 110.28 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05434 | 110.34 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05434 | 110.35 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05435 | 110.37 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05436 | 110.12 | P12:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05436 | 110.12 | P22:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05437 | 110.13 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05437 | 110.15 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05437 | 110.19 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05437 | 110.2 | P21:345:AMIL-MEC:AUTO-SINGLE:7SANDBURG:OAKGROV3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05438 | 110.16 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.11 | 655882 GALAXYTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.13 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.15 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.15 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.17 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.18 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.19 | P21:115:XEL:RED BUS #1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.2 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.2 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.2 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.21 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.22 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.39 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.46 | P13:230:EES:NINEMI:AT4 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.5 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.58 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.58 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.64 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.89 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.92 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 110.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 111.01 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 111.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 111.03 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 111.07 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 111.49 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 111.49 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 111.55 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 111.55 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 111.8 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 112.09 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 112.09 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 112.99 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 113.28 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 113.28 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 113.28 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 113.76 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 116.79 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0544 | 116.79 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05441 | 112.28 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05467 | 113.3 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05491 | 115.32 | Potential P4 Event - POI 774740_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05491 | 115.33 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05491 | 115.33 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05525 | 111.83 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05564 | 111.62 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05588 | 111.51 | P12:69:WERE:FRAN-NSES-69:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05671 | 115.09 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0568 | 111.73 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05701 | 113.2 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05831 | 112.21 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06283 | 114.71 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.06485 | 123.6 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07037 | 115.59 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07037 | 115.61 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.072 | 130.09 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08882 | 133.78 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08882 | 133.79 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.11665 | 132.99 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.77682 | 100.01 | 515254 SUNSTCN5 161 515265 SHAD-PT5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.77682 | 100.28 | P12:161:OKGE-SWPA-WFEC:BKRBKR4:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.77682 | 100.79 | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-056 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03978 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-056 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03978 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-056 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03978 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-057 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03482 | 110.99 | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-057 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03855 | 132.99 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-057 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04241 | 133.78 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-057 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04241 | 133.79 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24895 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29727 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29731 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29765 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29765 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29785 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29799 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.3006 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30745 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30817 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30902 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31519 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31519 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31927 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.33507 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.37454 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.14184 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.14184 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-061 | FROM->TO | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 223 | 223 | 0.25908 | 101.36 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-061 | FROM->TO | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 223 | 223 | 0.26033 | 100.13 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-061 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06444 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-061 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06444 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-061 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06444 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-063 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.11779 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-063 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.11779 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-063 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.11779 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.5423 | 100.01 | 515254 SUNSTCN5 161 515265 SHAD-PT5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.5423 | 100.28 | P12:161:OKGE-SWPA-WFEC:BKRBKR4:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.5423 | 100.79 | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-064 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.05167 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-064 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.05167 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-064 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.05167 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.17349 | 102.79 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-069 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.17349 | 102.79 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.17349 | 103.02 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-069 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.17349 | 103.02 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.03418 | 122.38 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03364 | 113.33 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03408 | 112.96 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03408 | 113.02 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03419 | 112.93 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03419 | 112.93 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03455 | 111.44 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03457 | 111.46 | P42:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03469 | 112.57 | P42:345:OKGE:SB_RARD7313:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03469 | 112.67 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03516 | 111.43 | P23:345:GMO:SIBLEY-R1-3:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03525 | 111.24 | P12:345:AMMO-GMO::OVERTON:SIBLEY:EHV | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03532 | 111.59 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03602 | 115.79 | P12:161:GRDA:MIAMI 5-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03605 | 110.73 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 116.25 | P12:161:GRDA:PENSA 5-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03611 | 111.19 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03611 | 111.26 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03611 | 111.28 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03629 | 110.3 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03631 | 111.95 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03634 | 110.23 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03634 | 110.23 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03635 | 110.38 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03636 | 111.08 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03638 | 110.34 | P23:345:MEC:BOONEVILLE:901:_1:: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03639 | 110.26 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03639 | 110.28 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0364 | 110.37 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03641 | 110.34 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03641 | 110.35 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03642 | 110.12 | P12:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03642 | 110.12 | P22:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03642 | 114.6 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03643 | 110.13 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03643 | 110.15 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03643 | 110.19 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03643 | 110.2 | P21:345:AMIL-MEC:AUTO-SINGLE:7SANDBURG:OAKGROV3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03644 | 110.16 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03644 | 110.45 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.11 | 655882 GALAXYTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.13 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.15 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.15 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.17 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.18 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.19 | P21:115:XEL:RED BUS #1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.2 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.2 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.21 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.22 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.39 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.46 | P13:230:EES:NINEMI:AT4 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.5 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.58 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.58 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.64 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.89 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.92 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.01 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.03 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.07 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.49 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.49 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.55 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.55 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.8 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 112.09 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 112.09 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 112.99 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 113.28 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 113.28 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 113.28 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 113.76 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 116.79 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 116.79 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03647 | 110.2 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03648 | 111.71 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03678 | 110.99 | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03686 | 112.28 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03695 | 113.3 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03719 | 111.83 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03724 | 115.32 | Potential P4 Event - POI 774740_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03724 | 115.33 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03724 | 115.33 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03742 | 111.62 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03762 | 111.51 | P12:69:WERE:FRAN-NSES-69:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0385 | 115.09 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0386 | 111.73 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03883 | 113.2 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04016 | 112.21 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04375 | 114.71 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04474 | 123.6 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05086 | 130.09 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0605 | 133.78 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0605 | 133.79 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07037 | 115.59 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07037 | 115.61 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-075 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08344 | 132.99 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.03418 | 122.38 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03364 | 113.33 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03408 | 112.96 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03408 | 113.02 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03419 | 112.93 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03419 | 112.93 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03455 | 111.44 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03457 | 111.46 | P42:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03469 | 112.57 | P42:345:OKGE:SB_RARD7313:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03469 | 112.67 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03516 | 111.43 | P23:345:GMO:SIBLEY-R1-3:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03525 | 111.24 | P12:345:AMMO-GMO::OVERTON:SIBLEY:EHV | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03532 | 111.59 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03602 | 115.79 | P12:161:GRDA:MIAMI 5-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03605 | 110.73 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03608 | 116.25 | P12:161:GRDA:PENSA 5-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03611 | 111.19 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03611 | 111.26 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03611 | 111.28 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03629 | 110.3 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03631 | 111.95 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03634 | 110.23 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03634 | 110.23 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03635 | 110.38 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03636 | 111.08 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03638 | 110.34 | P23:345:MEC:BOONEVILLE:901:_1:: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03639 | 110.26 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03639 | 110.28 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0364 | 110.37 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03641 | 110.34 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03641 | 110.35 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03642 | 110.12 | P12:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03642 | 110.12 | P22:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03642 | 114.6 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03643 | 110.13 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03643 | 110.15 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03643 | 110.19 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03643 | 110.2 | P21:345:AMIL-MEC:AUTO-SINGLE:7SANDBURG:OAKGROV3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03644 | 110.16 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03644 | 110.45 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.11 | 655882 GALAXYTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.13 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.15 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.15 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.17 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.18 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.19 | P21:115:XEL:RED BUS #1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.2 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.2 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.21 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.22 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.39 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.46 | P13:230:EES:NINEMI:AT4 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.5 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.58 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.58 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.64 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.89 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.92 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 110.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.01 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.03 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.07 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.49 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.49 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.55 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.55 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 111.8 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 112.09 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 112.09 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 112.99 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 113.28 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 113.28 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 113.28 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 113.76 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 116.79 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03646 | 116.79 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03647 | 110.2 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03648 | 111.71 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03678 | 110.99 | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03686 | 112.28 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03695 | 113.3 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03719 | 111.83 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03724 | 115.32 | Potential P4 Event - POI 774740_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03724 | 115.33 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03724 | 115.33 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03742 | 111.62 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03762 | 111.51 | P12:69:WERE:FRAN-NSES-69:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0385 | 115.09 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0386 | 111.73 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03883 | 113.2 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04016 | 112.21 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04375 | 114.71 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04474 | 123.6 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05086 | 130.09 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0605 | 133.78 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.0605 | 133.79 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07037 | 115.59 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07037 | 115.61 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-076 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.08344 | 132.99 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06823 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06823 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06823 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06823 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06823 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06823 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06823 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06823 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06823 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.16858 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21688 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21689 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21689 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21689 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21689 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21689 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21689 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21689 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21689 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21689 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21689 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21691 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21695 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21736 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21736 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21761 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21776 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21896 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21896 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21896 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22631 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22644 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22841 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22951 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22951 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22951 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22951 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23112 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23686 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23836 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23836 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24231 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25574 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25574 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25574 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25574 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27955 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.07781 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-081 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.07781 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-085 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03624 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-085 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03624 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-085 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.03624 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-086 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0442 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-086 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0442 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-086 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0442 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-088 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.05417 | 100.01 | 515254 SUNSTCN5 161 515265 SHAD-PT5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-088 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.05417 | 100.28 | P12:161:OKGE-SWPA-WFEC:BKRBKR4:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-088 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.05417 | 100.79 | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.17571 | 102.79 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-088 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.17571 | 102.79 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.17571 | 103.02 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-088 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.17571 | 103.02 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09605 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09605 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.09605 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.18899 | 102.79 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-092 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.18899 | 102.79 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.18899 | 103.02 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-092 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.18899 | 103.02 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-100 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0363 | 145.08 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-100 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0363 | 145.09 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-100 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0363 | 145.09 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-100 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04997 | 130.42 | Potential P4 Event - POI 515375_0 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-100 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04997 | 130.42 | Potential P4 Event - POI 515407_0 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-100 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0363 | 105.22 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-100 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0363 | 105.25 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-100 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0363 | 105.25 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.44782 | 145.08 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.44782 | 145.09 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.44782 | 145.09 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.45602 | 136.67 | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.4667 | 126.05 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47042 | 124.92 | Potential P4 Event - POI 515800_5 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47314 | 130.42 | Potential P4 Event - POI 515375_0 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47314 | 130.42 | Potential P4 Event - POI 515407_0 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47406 | 126.72 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47482 | 119.67 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47499 | 122.9 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47499 | 122.99 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47887 | 117.46 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47975 | 119.35 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47984 | 119.32 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47984 | 119.32 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.47984 | 119.37 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48099 | 120.52 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48102 | 120.72 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48106 | 118.88 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48106 | 120.22 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48129 | 122.73 | Potential P4 Event - POI 531449_3 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48206 | 115.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48234 | 116.2 | P12:138:AEPW:CHILD4WT:LAKEP4WT::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48236 | 116.6 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48236 | 116.85 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48236 | 116.88 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48277 | 116.54 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48277 | 117.1 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48288 | 115.35 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.483 | 114.37 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.483 | 114.37 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48312 | 113.9 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.4832 | 114.07 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48323 | 113.83 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.32 | P12:HV:EES::3PATMOS.W#:FULTON!:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.33 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.33 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.34 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.34 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.34 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.34 | P21:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.35 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.56 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.56 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.57 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.57 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.57 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.58 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.59 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.62 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.64 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.67 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.74 | 588671 G17-023XFMR1 34.5 588670 GEN-2017-023 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.77 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.87 | 508286 CAMPCOR4 138 765980 GEN-2021-075 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.87 | P13:138:EES:LC:T2 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.91 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.94 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.98 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.99 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.99 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 113.99 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.07 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.07 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.12 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.22 | 515192 LULA 4 138 772741 GEN-2023-038 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.33 | P13:230:EES:NINEMI:AT4 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.36 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.37 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.38 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.41 | P13:230:EES:NINEMI:AT5 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.44 | P11:26:EES:NINEMI:1(1) | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.44 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.46 | 508298 LYDIA 7 345 764075 GEN-2020-054 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.46 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.5 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.51 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.53 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.64 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 114.93 | P12:EHV:EES::8ANO%:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.15 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.15 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.19 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.19 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.22 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.22 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.37 | P11:25:EES:WATERF:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.37 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.37 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.68 | 775261 GEN-2023-164 345 775262 G23-164XFMR1 34.5 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.68 | 775261 GEN-2023-164 345 775282 G23-165XFMR1 34.5 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.68 | GEN-2023-164_POI_515800_Generator_outage | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 115.68 | GEN-2023-165_POI_515800_Generator_outage | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 116.67 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48327 | 117.92 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.48979 | 115.26 | 523771 GRAPEVINE 6 230 3WXFMR WAUK WT01089 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.44782 | 105.22 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.44782 | 105.25 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.44782 | 105.25 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.16072 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.16072 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.16072 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.16072 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.16072 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.16072 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.16072 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.16072 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.16072 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.10225 | 102.79 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.10225 | 102.79 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.10225 | 103.02 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.10225 | 103.02 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03029 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.03041 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0306 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-101 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04044 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-102 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0363 | 145.08 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-102 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0363 | 145.09 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-102 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0363 | 145.09 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-102 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04997 | 130.42 | Potential P4 Event - POI 515375_0 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-102 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04997 | 130.42 | Potential P4 Event - POI 515407_0 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-102 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0363 | 105.22 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-102 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0363 | 105.25 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-102 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0363 | 105.25 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03039 | 126.05 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03106 | 126.72 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03401 | 122.9 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03401 | 122.99 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03507 | 119.67 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03628 | 116.6 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03628 | 116.85 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03628 | 116.88 | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03634 | 120.52 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03637 | 122.73 | Potential P4 Event - POI 531449_3 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03648 | 118.88 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03648 | 120.22 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03655 | 120.72 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.33 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.33 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.34 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.34 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.34 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.34 | P21:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.35 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.56 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.56 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.58 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.59 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.62 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.64 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.67 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.74 | 588671 G17-023XFMR1 34.5 588670 GEN-2017-023 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.87 | 508286 CAMPCOR4 138 765980 GEN-2021-075 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.87 | P13:138:EES:LC:T2 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.91 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.94 | 588720 GEN-2017-117 138 771681 GEN-2022-235 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.98 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.99 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.99 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 113.99 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.07 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.07 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.12 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.22 | 515192 LULA 4 138 772741 GEN-2023-038 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.33 | P13:230:EES:NINEMI:AT4 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.36 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.37 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.38 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.41 | P13:230:EES:NINEMI:AT5 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.44 | P11:26:EES:NINEMI:1(1) | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.44 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.46 | 508298 LYDIA 7 345 764075 GEN-2020-054 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.46 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.5 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.51 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.53 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.64 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 114.93 | P12:EHV:EES::8ANO%:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.15 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.15 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.19 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.19 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.22 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.22 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.37 | P11:25:EES:WATERF:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.37 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.37 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.68 | 775261 GEN-2023-164 345 775262 G23-164XFMR1 34.5 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.68 | 775261 GEN-2023-164 345 775282 G23-165XFMR1 34.5 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.68 | GEN-2023-164_POI_515800_Generator_outage | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 115.68 | GEN-2023-165_POI_515800_Generator_outage | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 116.67 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03682 | 117.92 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03683 | 113.57 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03683 | 113.57 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03683 | 113.57 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03684 | 113.77 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03685 | 113.32 | P12:HV:EES::3PATMOS.W#:FULTON!:1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03685 | 115.26 | 523771 GRAPEVINE 6 230 3WXFMR WAUK WT01089 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03687 | 113.83 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03693 | 113.9 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.037 | 114.07 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03707 | 115.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03712 | 115.35 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03747 | 114.37 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03747 | 114.37 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03827 | 124.92 | Potential P4 Event - POI 515800_5 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03842 | 119.35 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03847 | 119.32 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03847 | 119.32 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03847 | 119.37 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03893 | 117.46 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03894 | 116.54 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03894 | 117.1 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04079 | 116.2 | P12:138:AEPW:CHILD4WT:LAKEP4WT::: | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05324 | 130.42 | Potential P4 Event - POI 515375_0 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05324 | 130.42 | Potential P4 Event - POI 515407_0 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05383 | 145.08 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05383 | 145.09 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05383 | 145.09 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05383 | 105.22 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05383 | 105.25 | Potential P4 Event - POI 762216_14 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05383 | 105.25 | Potential P4 Event - POI 762467_7 | TDF Impact | Sweetwater to Demarcation 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.1975 | 102.79 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.1975 | 102.79 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.1975 | 103.02 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-104 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.1975 | 103.02 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-105 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.06119 | 100.16 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-105 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.06119 | 100.16 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-105 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.06119 | 101.46 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-105 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.06119 | 101.57 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-105 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.08931 | 102.18 | Potential P4 Event - POI 659105_8 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-105 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.08945 | 100.55 | 659105 LELAND_O-BE3 345 659424 LO.LS-CC-BE3 345 Z | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-105 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.08945 | 100.61 | 659424 LO.LS-CC-BE3 345 764220 G20-021-TAP 345 1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-105 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.08945 | 100.61 | P12:345:UMZB:# 7129 #:: CHA IN SD. LOS - CHAPPELLE CREEK 345:EHV: | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-105 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.08945 | 100.61 | P14:345:UMZ:# 7213 #:: PROPER TAKE LINE WITH LELAND OLDS-FORT THOMPSON LINE REACTOR:EHV: | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-105 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.09457 | 107.96 | Potential P4 Event - POI 659105_15 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-105 | FROM->TO | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 239 | 239 | 0.09457 | 100.31 | Potential P4 Event - POI 659105_15 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-134 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.04913 | 100.01 | 515254 SUNSTCN5 161 515265 SHAD-PT5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-134 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.04913 | 100.28 | P12:161:OKGE-SWPA-WFEC:BKRBKR4:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-134 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.04913 | 100.79 | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-134 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14927 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-134 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14927 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-134 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14927 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.3986 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.3986 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.3986 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24895 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29727 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29731 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29765 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29765 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29785 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29799 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.3006 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30745 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30817 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30902 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31519 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31519 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31927 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.33507 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.37454 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.14184 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.14184 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05581 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24895 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29726 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29727 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29731 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29765 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29765 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29785 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29799 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29899 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.3006 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30745 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30773 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30817 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30902 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31167 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31519 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31519 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31927 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.33507 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.37454 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.14184 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.14184 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-149 | FROM->TO | 542965 W.GRDNR7 345 997212 WEST GARDN11 161 11 | 535 | 535 | 0.09813 | 103.86 | Potential P4 Event - POI 542940_3 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-149 | FROM->TO | 542965 W.GRDNR7 345 997212 WEST GARDN11 161 11 | 535 | 535 | 0.09813 | 104.55 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-149 | FROM->TO | 542965 W.GRDNR7 345 997212 WEST GARDN11 161 11 | 535 | 535 | 0.11569 | 116.76 | Potential P4 Event - POI 542965_4 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 997212 WEST GARDN11 161 11 | 535 | 535 | 0.09813 | 103.77 | Potential P4 Event - POI 542940_3 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 997212 WEST GARDN11 161 11 | 535 | 535 | 0.09813 | 104.43 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-149 | FROM->TO | 542966 WGARDNR5 161 997212 WEST GARDN11 161 11 | 535 | 535 | 0.11569 | 116.48 | Potential P4 Event - POI 542965_4 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-149 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 311 | 334 | 0.11675 | 102.02 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.07049 | 100.24 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.07049 | 100.24 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.07112 | 100.32 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.07112 | 100.32 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.07654 | 101.52 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.07654 | 101.52 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.42465 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.42465 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.42465 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.42465 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.42465 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.42465 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.42465 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.42465 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.42465 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 183 | 201 | 0.11046 | 100.32 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 183 | 201 | 0.11046 | 100.32 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.10062 | 101.26 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.10062 | 101.26 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.10141 | 101.28 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.10141 | 101.28 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.10255 | 100.04 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.10255 | 100.04 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.11046 | 103.56 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.11046 | 103.56 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03331 | 107.82 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03331 | 107.97 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03422 | 105.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03453 | 106.36 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03524 | 107.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03524 | 107.1 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03566 | 103.24 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03566 | 103.34 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03566 | 103.45 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.15 | 300120 5THMHILB1 161 301504 5THOMHLGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.15 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.16 | 344011 7HUGHES 345 344012 7HPW-N 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.17 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.2 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.22 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.26 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.28 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.3 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.3 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.3 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.32 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.34 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.37 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.37 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.38 | P11:20:AMMO:1LAB G1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.38 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.41 | P13:MR#2 GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.42 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.42 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.44 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.46 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.47 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.49 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.53 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.54 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.55 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.66 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.71 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.78 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.79 | 773981 GEN-2023-100 345 773985 G23-100XFMR2 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.79 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.8 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.84 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.88 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.96 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.96 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.02 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.03 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.04 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.05 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.05 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.07 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.17 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.18 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.23 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.3 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.3 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.31 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.38 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.39 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.41 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.69 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.7 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.77 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 105.07 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 105.67 | GEN-2008-051_POI_523961_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 107.37 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03568 | 103.09 | P12:HV:EES::3COUCH%:3LEWISVILLE#:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03568 | 103.25 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03569 | 103.37 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0357 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03572 | 103.62 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03616 | 106.98 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03785 | 103.84 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04393 | 108.56 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04393 | 108.56 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04393 | 108.6 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04393 | 109.91 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 123.96 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.18 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.18 | Potential P4 Event - POI 515458_6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.18 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.18 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.18 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.51 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06015 | 118.76 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06548 | 118.05 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06548 | 118.05 | Potential P4 Event - POI 514801_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06664 | 118.14 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06812 | 117.64 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03331 | 108.34 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03331 | 108.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03422 | 105.98 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03453 | 106.81 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03524 | 107.82 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03524 | 107.83 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03566 | 103.9 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03566 | 104 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03566 | 104.12 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.81 | 300120 5THMHILB1 161 301504 5THOMHLGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.81 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.82 | 344011 7HUGHES 345 344012 7HPW-N 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.84 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.87 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.89 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.92 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.92 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.94 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.94 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.96 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.96 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 103.99 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.01 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.02 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.02 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.04 | P11:20:AMMO:1LAB G1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.04 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.08 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.08 | P13:MR#2 GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.09 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.11 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.13 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.14 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.16 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.17 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.19 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.2 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.22 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.37 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.44 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.44 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.45 | 773981 GEN-2023-100 345 773985 G23-100XFMR2 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.46 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.48 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.51 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.61 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.61 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.67 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.68 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.69 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.7 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.7 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.71 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.82 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.82 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.87 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.94 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.94 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 104.94 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 105.01 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 105.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 105.05 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 105.29 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 105.31 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 105.44 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 105.74 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 106.64 | GEN-2008-051_POI_523961_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03567 | 107.84 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03568 | 103.91 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03569 | 104.03 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0357 | 103.58 | P12:EHV:EES::7SAREPTA%:7EL DORADO:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0357 | 104.24 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03572 | 104.28 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03616 | 107.52 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03785 | 104.48 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04393 | 108.91 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04393 | 108.91 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04393 | 108.95 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2