Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10709 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10709 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10719 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1072 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10722 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10738 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10745 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10745 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10746 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10746 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10747 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10805 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10805 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10807 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10814 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10817 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10821 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10821 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1083 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10831 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10885 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10925 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10958 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10959 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11075 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11081 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11097 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11158 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11158 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11158 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11163 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.112 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.112 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11262 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11332 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11429 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11429 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11654 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11997 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12075 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12075 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19615 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14485 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14712 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14729 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14847 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15019 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15019 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15021 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15033 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15038 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15045 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15045 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15065 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15068 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15157 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15223 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15251 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15251 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15251 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15286 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15287 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15457 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15467 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1548 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15494 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15496 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15501 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15531 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15531 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15757 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15765 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15765 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15789 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15789 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15865 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16061 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17208 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25764 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28123 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28313 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28313 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28313 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28313 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28466 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.13498 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.15788 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25742 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28094 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28283 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28283 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28283 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28283 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28438 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12213 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12253 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12253 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12268 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12275 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12276 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12276 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12279 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12279 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12279 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12283 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12283 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12286 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12286 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12286 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12287 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12289 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12289 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.123 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12301 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12304 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12321 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12329 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1233 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12331 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12331 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12332 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12398 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12398 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12401 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12409 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12412 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12417 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12417 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12429 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12434 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1249 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12537 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12574 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12575 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12598 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12708 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12715 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12734 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12803 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12803 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12803 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12809 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12852 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12852 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12924 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13003 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13114 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13114 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13373 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13767 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13856 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13856 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2033 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10643 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10678 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10678 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10691 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10698 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10698 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.107 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.107 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10704 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10704 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10707 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10707 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10707 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10708 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10708 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10709 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10709 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10719 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1072 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10722 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10738 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10745 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10745 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10746 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10746 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10747 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10805 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10805 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10807 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10814 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10817 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10821 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10821 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10831 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10885 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10925 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10958 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10959 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10978 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11075 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11081 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11097 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11158 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11158 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11158 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11163 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.112 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.112 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11262 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11332 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11429 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11429 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11654 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11997 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12054 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12075 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12075 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19615 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08045 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08346 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05206 | 115.41 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05206 | 115.42 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05206 | 115.42 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05206 | 115.46 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05206 | 115.46 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05206 | 114.08 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05206 | 114.1 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05206 | 114.1 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05206 | 114.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05206 | 114.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.082 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08699 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.08336 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.08443 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.08336 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.08443 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14084 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21383 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21597 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21597 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21612 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21619 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2162 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2162 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21622 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21622 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21623 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21623 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21627 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21627 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2164 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21641 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21647 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21661 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21663 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21669 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21669 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21672 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2172 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21732 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21733 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21733 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21736 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2175 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21751 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21751 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21823 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21823 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21827 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21827 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21863 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21995 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21998 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22004 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22021 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22041 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22041 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22137 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22148 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22188 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22262 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22262 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22472 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22618 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22741 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22741 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35803 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12274 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18634 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18821 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18821 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18834 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1884 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18841 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18843 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18843 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18847 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18847 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18851 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18851 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18851 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18851 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18859 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1886 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18864 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18877 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18879 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18883 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18883 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18887 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18928 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18936 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18938 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18939 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18939 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18942 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18955 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18955 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18955 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19018 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19018 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19021 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19022 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19053 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19168 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19171 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19175 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19191 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19208 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19208 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19292 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19302 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19336 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19401 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19401 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19584 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1971 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19818 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19818 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.34543 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1238 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23236 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23274 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2329 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23292 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23292 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23301 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23316 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23317 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23317 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23356 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23428 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23438 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23439 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23485 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23583 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23587 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23587 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23634 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23634 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23663 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23675 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23701 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23704 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23707 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23857 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23932 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23939 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23939 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24064 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24239 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24239 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24239 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24809 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24937 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42328 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.43473 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.43717 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44116 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44116 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44116 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44116 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22762 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2288 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42291 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.43431 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.43673 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4407 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4407 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4407 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4407 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14084 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21383 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21597 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21597 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21612 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21619 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2162 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2162 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21622 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21622 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21623 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21627 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21627 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2164 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21641 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21647 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21661 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21663 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21669 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21669 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21672 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2172 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21732 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21733 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21733 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2175 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21751 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21751 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21823 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21823 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21827 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21827 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21831 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21863 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21995 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21998 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22004 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22021 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22041 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22041 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22137 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22148 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22188 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22262 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22262 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22472 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22618 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22741 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22741 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35803 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12274 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18634 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18821 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18821 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18834 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1884 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18841 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18843 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18843 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18847 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18847 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18851 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18851 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18851 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18851 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18859 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1886 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18864 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18877 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18879 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18883 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18883 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18887 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18928 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18936 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18938 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18939 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18939 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18955 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18955 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18955 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19018 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19018 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19021 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19022 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19025 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19053 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19168 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19171 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19175 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19191 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19208 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19208 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19292 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19302 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19336 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19401 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19401 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19584 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1971 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19803 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19818 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19818 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.34543 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06952 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07028 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05497 | 115.41 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05497 | 115.42 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05497 | 115.42 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05497 | 115.46 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05497 | 115.46 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05497 | 114.08 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05497 | 114.1 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05497 | 114.1 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05497 | 114.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05497 | 114.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 185 | 210 | 1 | 133.27 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 185 | 210 | 1 | 132.5 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0832 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08747 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08747 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08763 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0877 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0877 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0877 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0877 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0877 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08773 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08773 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08773 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08773 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08778 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08778 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08781 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08781 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08781 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08781 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08784 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08784 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08797 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08798 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08798 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08817 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08829 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08829 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0883 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0884 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0886 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08902 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08902 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08921 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08921 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08924 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08926 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08928 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08933 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08936 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08937 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08985 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09035 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09046 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09047 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09267 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09273 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09292 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09508 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09552 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09595 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09595 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09635 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09635 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09742 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09792 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1012 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10221 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10221 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14525 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07251 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07623 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07623 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07636 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07642 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07642 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07642 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07642 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07643 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07645 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07645 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07649 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07649 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07652 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07653 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07653 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07653 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07653 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07655 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07655 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07667 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07667 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07667 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07684 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07694 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07694 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07695 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07703 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07721 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07758 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07758 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07775 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07775 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07777 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07779 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0778 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07784 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07787 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07788 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0783 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07874 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07884 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07884 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08076 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08081 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08098 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08286 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08324 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08361 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08361 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08397 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08397 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08489 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08533 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0882 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08907 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08907 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14013 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10179 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10677 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10897 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11134 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11134 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11134 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11135 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1132 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1132 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11347 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11347 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1135 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1136 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11362 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11367 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11369 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11446 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11517 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11541 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11543 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11837 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11844 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11872 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11873 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1188 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11968 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11968 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12064 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12115 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12115 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12172 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12181 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12181 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12388 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12565 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13302 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1894 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2113 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21233 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21233 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21233 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21233 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2167 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.09339 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.12205 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18923 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21108 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21211 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21211 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21211 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21211 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21649 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0832 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08747 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08747 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08763 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0877 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0877 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0877 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0877 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0877 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08773 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08773 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08773 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08778 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08778 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08781 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08781 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08781 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08781 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08784 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08784 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08797 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08798 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08798 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08817 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08829 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08829 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0883 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0884 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0886 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08902 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08902 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08921 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08921 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08924 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08928 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08933 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08936 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08937 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08985 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09032 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09035 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09046 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09047 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09267 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09273 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09292 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09508 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09552 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09595 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09595 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09635 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09635 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09742 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09792 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1012 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10168 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10221 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10221 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14525 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07251 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07623 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07623 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07636 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07642 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07642 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07642 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07642 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07643 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07645 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07645 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07649 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07649 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07652 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07653 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07653 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07653 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07653 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07655 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07655 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07667 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07667 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07667 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07684 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07694 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07694 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07695 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07703 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07721 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07758 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07758 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07775 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07775 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07777 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0778 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07784 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07787 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07788 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0783 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07871 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07874 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07884 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07884 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08076 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08081 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08098 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08286 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08324 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08361 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08361 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08397 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08397 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08489 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08533 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0882 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08861 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08907 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08907 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14013 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08561 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12885 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13563 | 101.14 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.05 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.5 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.5 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13804 | 109.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13804 | 109.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13838 | 109.93 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17197 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17572 | 110.53 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 111.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 112.37 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 112.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18641 | 113.15 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18641 | 113.15 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18677 | 113.77 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0809 | 104.62 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 105.24 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 105.59 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 105.84 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 105.84 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08967 | 106.03 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 106.06 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 109.93 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10284 | 116.31 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12885 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0809 | 103.54 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08643 | 104.65 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 103.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 104.24 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 104.5 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 104.5 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08967 | 104.7 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 108.19 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10284 | 114.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10959 | 143.58 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14889 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14981 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14984 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14991 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14995 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14995 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15002 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15004 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15006 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15007 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15015 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15019 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15019 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1502 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15045 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1505 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15051 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15052 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15052 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1506 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15061 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15062 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15062 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15084 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15098 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15098 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15106 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15192 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15197 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15206 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15264 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15298 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15371 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15371 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15603 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15613 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15667 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15767 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15767 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16105 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1663 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16889 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19833 | 172.27 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19833 | 172.27 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19856 | 172.75 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10095 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17442 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17623 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1763 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17641 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17652 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17653 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17658 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17665 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17675 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17684 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17733 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17741 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17744 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17755 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17836 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17878 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17893 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17911 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1801 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18018 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18036 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18154 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18183 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18204 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19587 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08797 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.152 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15358 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15383 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15384 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15388 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15395 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15403 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15411 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15453 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15461 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15463 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15473 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15544 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1558 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15593 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15609 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15695 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15702 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15718 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1582 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15846 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15864 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17069 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1751 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11163 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22059 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22071 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22076 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22096 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22215 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22228 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22267 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22268 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22274 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22389 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22452 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22464 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22489 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22493 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22496 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22648 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22723 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22908 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23886 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26059 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37603 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41286 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4143 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21915 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23909 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3757 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41245 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41387 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10095 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17442 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17623 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1763 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17641 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17652 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17653 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17658 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17665 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17675 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17684 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17733 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17741 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17744 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17803 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17836 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17878 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17893 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17911 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1801 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18018 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18036 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18154 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18183 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18204 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19587 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08797 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.152 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15358 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15383 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15384 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15388 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15395 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15403 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15411 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15453 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15461 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15463 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15515 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15544 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1558 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15593 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15609 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15695 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15702 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15718 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1582 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15846 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15864 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17069 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1751 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08561 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12885 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13563 | 101.14 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.05 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.5 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.5 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13804 | 109.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13804 | 109.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13838 | 109.93 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17197 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17572 | 110.53 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 111.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 112.37 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 112.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18641 | 113.15 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18641 | 113.15 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18677 | 113.77 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0809 | 104.62 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 105.24 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 105.59 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 105.84 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 105.84 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08967 | 106.03 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 106.06 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 109.93 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10284 | 116.31 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12885 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0809 | 103.54 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08643 | 104.65 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 103.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 104.24 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 104.5 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 104.5 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08967 | 104.7 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 108.19 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10284 | 114.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10959 | 143.58 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14889 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14981 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14984 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14991 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14995 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14995 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15002 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15004 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15006 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15007 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15015 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15019 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15019 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1502 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15045 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1505 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15051 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15052 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15052 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1506 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15061 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15062 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15062 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15084 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15098 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15098 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15106 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15192 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15197 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15206 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15264 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15298 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15371 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15371 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15603 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15613 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15667 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15767 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15767 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16105 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1663 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16889 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19833 | 172.27 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19833 | 172.27 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19856 | 172.75 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10095 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17442 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17623 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1763 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17641 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17652 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17653 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17658 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17665 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17675 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17684 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17733 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17741 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17744 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17755 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17836 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17878 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17893 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17911 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1801 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18018 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18036 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18154 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18183 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18204 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19587 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08797 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.152 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15358 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15383 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15384 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15388 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15395 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15403 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15411 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15453 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15461 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15463 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15473 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15544 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1558 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15593 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15609 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15695 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15702 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15718 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1582 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15846 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15864 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17069 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1751 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11163 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22059 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22071 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22076 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22096 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22215 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22228 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22267 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22268 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22274 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22389 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22452 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22464 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22489 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22493 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22496 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22648 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22723 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22908 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23886 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26059 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37603 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41286 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4143 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21915 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23909 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3757 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41245 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41387 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10095 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17442 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17623 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1763 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17641 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17652 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17653 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17658 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17665 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17675 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17684 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17733 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17741 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17744 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17803 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17836 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17878 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17893 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17911 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1801 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18018 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18036 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18154 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18183 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18204 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19587 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08797 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.152 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15358 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15383 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15384 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15388 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15395 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15403 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15411 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15453 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15461 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15463 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15515 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15544 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1558 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15593 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15609 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15695 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15702 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15718 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1582 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15846 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15864 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17069 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1751 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08598 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09418 | 101.14 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09824 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10552 | 108.05 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10552 | 108.5 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10552 | 108.5 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10586 | 109.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10586 | 109.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10629 | 109.93 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13035 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13332 | 110.53 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14297 | 111.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14297 | 112.37 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14297 | 112.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1433 | 113.15 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1433 | 113.15 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14375 | 113.77 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05036 | 106.06 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05036 | 109.93 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05349 | 105.24 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05349 | 105.59 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05356 | 105.84 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05356 | 105.84 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05364 | 106.03 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05801 | 116.31 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09824 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05036 | 108.19 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05077 | 104.65 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05349 | 103.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05349 | 104.24 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05356 | 104.5 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05356 | 104.5 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05364 | 104.7 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05801 | 114.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.12682 | 143.58 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16608 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16703 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16707 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16713 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16718 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16718 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1672 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1672 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1672 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16721 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16721 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16721 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16721 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16725 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16727 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16728 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1673 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16738 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16741 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16741 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16743 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16767 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16772 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16774 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16775 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16775 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16782 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16783 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16784 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16784 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16793 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16808 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16808 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16829 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16851 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16853 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16853 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16914 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16918 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16928 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1698 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17001 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17018 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17031 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17092 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17092 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17372 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17429 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.175 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.175 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18178 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18942 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19675 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21841 | 172.27 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21841 | 172.27 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21869 | 172.75 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.2153 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21807 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.2153 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21807 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16429 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16603 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16603 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16618 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16625 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16625 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16626 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16628 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16628 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16629 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16629 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16633 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16633 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16646 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16648 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16653 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16658 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16669 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16675 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16675 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16678 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16726 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16738 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16739 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16739 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16749 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16756 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16757 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16757 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16807 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16831 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1685 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16872 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16893 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16893 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17002 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1701 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17028 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17136 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17307 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17307 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17961 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17961 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18093 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18922 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19757 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27533 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14318 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14469 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14469 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14482 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14488 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14488 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14491 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14491 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14495 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14495 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14507 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14508 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14512 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14517 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14527 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14532 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14532 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14534 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14576 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14583 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14586 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14587 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14587 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14596 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14602 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14603 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14603 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14647 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14668 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14684 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14697 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14698 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14704 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14722 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14722 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14816 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14824 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14839 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14933 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14985 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15083 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15083 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15767 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1649 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17217 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26564 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11412 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22306 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22318 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22321 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22321 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22323 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22325 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22325 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22344 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22348 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2235 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2235 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22432 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22463 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22483 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22483 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22518 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22519 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22522 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22697 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22709 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22734 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22738 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22741 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22786 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2288 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22966 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22973 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22973 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23153 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24161 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27028 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36974 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4174 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41898 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22167 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24798 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36942 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41699 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41856 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16429 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16603 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16603 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16618 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16625 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16625 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16626 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16628 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16628 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16629 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16633 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16633 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16646 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16648 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16653 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16658 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16669 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16675 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16675 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16678 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16726 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16738 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16739 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16739 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16756 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16757 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16757 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16781 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16807 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16831 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1685 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16872 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16893 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16893 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17002 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1701 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17028 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17136 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17307 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17307 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17961 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17961 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18093 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18922 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19757 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27533 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14318 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14469 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14469 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14482 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14488 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14488 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14491 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14491 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14495 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14495 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14507 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14508 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14512 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14517 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14527 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14532 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14532 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14534 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14576 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14583 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14586 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14587 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14587 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14602 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14603 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14603 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14624 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14647 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14668 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14684 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14697 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14698 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14704 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14722 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14722 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14816 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14824 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14839 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14933 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14985 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15083 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15083 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15767 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1649 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17217 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26564 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0813 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08598 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09418 | 101.14 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09824 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10552 | 108.05 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10552 | 108.5 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10552 | 108.5 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10586 | 109.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10586 | 109.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10629 | 109.93 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13035 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13332 | 110.53 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14297 | 111.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14297 | 112.37 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14297 | 112.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1433 | 113.15 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1433 | 113.15 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14375 | 113.77 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05036 | 106.06 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05036 | 109.93 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05349 | 105.24 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05349 | 105.59 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05356 | 105.84 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05356 | 105.84 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05364 | 106.03 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05801 | 116.31 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09824 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05036 | 108.19 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05077 | 104.65 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05349 | 103.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05349 | 104.24 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05356 | 104.5 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05356 | 104.5 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05364 | 104.7 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05801 | 114.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.12682 | 143.58 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16608 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16703 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16707 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16713 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16718 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16718 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1672 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1672 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1672 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16721 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16721 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16721 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16721 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16725 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16727 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16728 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1673 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16738 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16741 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16741 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16743 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16767 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16772 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16774 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16775 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16775 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16782 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16783 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16784 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16784 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16793 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16808 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16808 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16829 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16851 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16853 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16853 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16914 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16918 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16928 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1698 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17001 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17018 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17031 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17092 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17092 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17372 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17429 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.175 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.175 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18178 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18414 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18942 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19675 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21841 | 172.27 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21841 | 172.27 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21869 | 172.75 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.2153 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21807 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.2153 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21807 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16429 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16603 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16603 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16618 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16625 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16625 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16626 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16628 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16628 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16629 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16629 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16633 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16633 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16646 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16648 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16653 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16658 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16669 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16675 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16675 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16678 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16726 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16738 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16739 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16739 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16749 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16756 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16757 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16757 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16807 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16831 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1685 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16872 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16893 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16893 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17002 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1701 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17028 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17136 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17307 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17307 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17961 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17961 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18093 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18922 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19757 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27533 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14318 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14469 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14469 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14482 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14488 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14488 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14491 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14491 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14495 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14495 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14507 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14508 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14512 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14517 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14527 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14532 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14532 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14534 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14576 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14583 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14586 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14587 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14587 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14596 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14602 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14603 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14603 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14647 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14668 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14684 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14697 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14698 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14704 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14722 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14722 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14816 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14824 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14839 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14933 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14985 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15083 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15083 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15767 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1649 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17217 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26564 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11412 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22306 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22318 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22321 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22321 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22323 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22325 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22325 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22344 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22348 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2235 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2235 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22432 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22463 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22483 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22483 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22518 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22519 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22522 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22697 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22709 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22734 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22738 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22741 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22786 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2288 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22966 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22973 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22973 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23153 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24161 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27028 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36974 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4174 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41898 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22167 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24798 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36942 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41699 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41856 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16429 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16603 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16603 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16618 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16625 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16625 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16626 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16628 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16628 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16629 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16633 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16633 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16635 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16637 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16646 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16648 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16653 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16658 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16669 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16675 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16675 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16678 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16726 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16738 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16739 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16739 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16756 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16757 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16757 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16781 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16807 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16831 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1685 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16872 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16893 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16893 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17002 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1701 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17028 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17136 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17307 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17307 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17961 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17961 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18093 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18922 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19757 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1985 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27533 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14318 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14469 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14469 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14482 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14488 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14488 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14491 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14491 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14495 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14495 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14497 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14499 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14507 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14508 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14512 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14517 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14527 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14532 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14532 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14534 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14576 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14583 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14586 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14587 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14587 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14602 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14603 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14603 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14624 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14647 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14668 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14684 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14697 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14698 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14704 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14722 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14722 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14816 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14824 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14839 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14933 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14985 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15083 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15083 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15767 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1649 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17217 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17298 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17731 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26564 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08561 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12885 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13563 | 101.14 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.05 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.5 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.5 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13804 | 109.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13804 | 109.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13838 | 109.93 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17197 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17572 | 110.53 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 111.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 112.37 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 112.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18641 | 113.15 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18641 | 113.15 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18677 | 113.77 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0809 | 104.62 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 105.24 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 105.59 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 105.84 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 105.84 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08967 | 106.03 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 106.06 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 109.93 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10284 | 116.31 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12885 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0809 | 103.54 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08643 | 104.65 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 103.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 104.24 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 104.5 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 104.5 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08967 | 104.7 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 108.19 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10284 | 114.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10959 | 143.58 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14889 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14981 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14984 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14991 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14995 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14995 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15002 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15004 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15006 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15007 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15015 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15019 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15019 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1502 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15045 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1505 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15051 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15052 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15052 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1506 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15061 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15062 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15062 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15084 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15098 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15098 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15106 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15192 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15197 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15206 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15264 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15298 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15371 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15371 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15603 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15613 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15667 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15767 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15767 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16105 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1663 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16889 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19833 | 172.27 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19833 | 172.27 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19856 | 172.75 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10095 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17442 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17623 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1763 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17641 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17652 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17653 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17658 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17665 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17675 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17684 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17733 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17741 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17744 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17755 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17836 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17878 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17893 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17911 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1801 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18018 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18036 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18154 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18183 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18204 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19587 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08797 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.152 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15358 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15383 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15384 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15388 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15395 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15403 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15411 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15453 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15461 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15463 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15473 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15544 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1558 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15593 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15609 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15695 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15702 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15718 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1582 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15846 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15864 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17069 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1751 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11163 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22059 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22071 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22076 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22096 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22215 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22228 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22267 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22268 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22274 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22389 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22452 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22464 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22489 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22493 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22496 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22648 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22723 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22908 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23886 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26059 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37603 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41286 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4143 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21915 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23909 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3757 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41245 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41387 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10095 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17442 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17623 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1763 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17641 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17652 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17653 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17658 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17665 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17675 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17684 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17733 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17741 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17744 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17803 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17836 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17878 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17893 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17911 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1801 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18018 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18036 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18154 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18183 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18204 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19587 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08797 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.152 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15358 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15383 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15384 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15388 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15395 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15403 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15411 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15453 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15461 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15463 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15515 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15544 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1558 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15593 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15609 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15695 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15702 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15718 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1582 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15846 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15864 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17069 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1751 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0806 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.085 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.0709 | 101.14 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.07628 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08146 | 108.05 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08146 | 108.5 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08146 | 108.5 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08175 | 109.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08175 | 109.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08226 | 109.93 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.12231 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1245 | 110.53 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13225 | 111.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13225 | 112.37 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13225 | 112.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13253 | 113.15 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13253 | 113.15 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13306 | 113.77 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.07628 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.12192 | 143.58 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16133 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16214 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16217 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16224 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16229 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16229 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1623 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1623 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1623 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16231 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16231 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16232 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16232 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16236 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16237 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16239 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1624 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16249 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16252 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16252 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16253 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16279 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16283 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16285 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16286 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16286 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16286 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16294 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16295 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16295 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16295 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1631 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16325 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16325 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1634 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16363 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16368 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16368 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16427 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16431 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16438 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16441 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.165 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16532 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16613 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16613 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16835 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16887 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17035 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17035 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17382 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17556 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1772 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1772 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1772 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1772 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1772 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1772 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1845 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20962 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20962 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20962 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20975 | 172.27 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20975 | 172.27 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21007 | 172.75 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.19953 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20211 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.19953 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20211 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09036 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16403 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16549 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16549 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16564 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16571 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16572 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16572 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16574 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16574 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16575 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16575 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16579 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16579 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16581 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16581 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16581 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16583 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16583 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16583 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16593 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16594 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16599 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16605 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16616 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16622 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16622 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16625 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16674 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16683 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16686 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16686 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16686 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16699 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16704 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16704 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16704 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16778 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1678 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16814 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16819 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1682 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1682 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16856 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16856 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16953 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16961 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.171 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17146 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17148 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17272 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17272 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1795 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1795 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18865 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19318 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27444 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07874 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14294 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14422 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14422 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14435 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14441 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14441 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14444 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14444 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14448 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14448 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1445 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1445 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1445 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14452 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14452 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14452 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14452 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1446 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14461 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14465 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14471 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1448 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14485 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14485 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14488 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14531 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14538 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14541 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14541 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14541 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14552 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14557 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14557 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14557 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14622 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14623 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14652 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14657 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14658 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14658 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1469 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1469 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14774 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14781 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14797 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14902 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14942 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14944 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15052 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15052 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15643 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15643 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1644 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16835 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17446 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17446 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17446 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26478 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10646 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21145 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21543 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21555 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21559 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2156 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2156 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21578 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21578 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21582 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21585 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21585 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21585 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21687 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21699 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21737 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21737 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21758 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21764 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21937 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21949 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21975 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21978 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21982 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22068 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22138 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2221 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22217 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22217 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22414 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23459 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24045 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24045 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24045 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26256 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36152 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40353 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40456 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40809 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40809 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40809 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40809 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21523 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2409 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36121 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40313 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40415 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40767 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40767 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40767 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40767 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09036 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16403 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16549 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16549 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16564 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16571 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16572 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16572 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16574 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16574 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16575 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16579 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16579 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16581 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16581 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16581 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16583 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16583 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16583 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16593 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16594 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16599 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16605 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16616 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16622 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16622 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16625 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16674 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16683 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16686 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16686 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16686 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16704 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16704 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16704 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16778 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1678 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16814 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16819 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1682 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1682 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16856 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16856 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16953 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16961 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.171 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17146 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17148 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17272 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17272 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1795 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1795 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18865 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19318 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19408 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27444 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07874 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14294 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14422 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14422 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14435 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14441 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14441 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14444 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14444 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14448 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14448 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1445 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1445 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1445 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14452 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14452 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14452 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14452 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1446 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14461 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14465 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14471 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1448 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14485 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14485 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14488 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14531 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14538 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14541 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14541 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14541 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14557 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14557 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14557 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14583 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14622 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14623 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14652 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14657 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14658 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14658 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1469 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1469 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14774 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14781 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14797 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14902 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14942 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14944 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15052 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15052 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15643 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15643 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1644 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16835 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16914 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17446 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17446 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17446 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26478 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.076 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07856 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05961 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07821 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05961 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05777 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05792 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05801 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06072 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06075 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06082 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06087 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06087 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06089 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06089 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06089 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0609 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0609 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0609 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0609 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06095 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06096 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06096 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06097 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06099 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06107 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06112 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06112 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06112 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06119 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06138 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06143 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06146 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06146 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06147 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06149 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06153 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06153 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06156 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06156 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06159 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0616 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06168 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06203 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06227 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06272 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06273 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06299 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06303 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06313 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.064 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0641 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06553 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06553 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07135 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07187 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07187 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08257 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08257 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08257 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08257 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08257 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08257 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10616 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07134 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07134 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07134 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08579 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08589 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0871 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0871 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08725 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08732 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08733 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08733 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08736 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08736 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08736 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08736 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0874 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0874 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08743 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08743 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08743 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08744 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08745 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08745 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08755 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08757 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08759 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08761 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08778 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08786 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08786 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08788 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08846 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08852 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08852 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08855 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08858 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0887 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0887 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0888 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08886 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0889 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08932 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08932 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08948 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08993 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09061 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09062 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0914 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09148 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09166 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09341 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09346 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0958 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0958 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10609 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10609 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12798 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13406 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14463 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06217 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06217 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06217 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07476 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07485 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0759 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0759 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07604 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0761 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0761 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07611 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07613 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07613 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07617 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07617 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07619 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07619 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07619 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0762 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07621 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07621 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07621 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0763 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07632 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07633 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07635 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0765 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07657 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07657 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07658 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07709 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07714 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07714 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07717 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07719 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0773 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0773 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07739 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07744 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07747 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07784 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07784 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07798 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07837 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07896 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07897 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07965 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07972 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07988 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08141 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08144 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08349 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08349 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09246 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09246 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11153 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11683 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13954 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.05369 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14039 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14896 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14896 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14896 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1599 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1599 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16123 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16282 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1629 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1629 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16293 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16298 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16308 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16316 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16316 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16329 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16344 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16359 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16359 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16434 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16499 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16606 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16607 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16697 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16709 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16735 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16737 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16742 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16974 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16984 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16992 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16992 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1735 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18927 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20852 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2395 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2602 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30529 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30746 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30746 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30746 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30746 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30823 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.17366 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23873 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23929 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30497 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30715 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30715 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30715 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30715 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30792 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07134 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07134 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07134 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08579 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08589 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0871 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0871 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08725 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08732 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08733 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08733 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08736 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08736 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08736 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0874 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0874 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08743 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08743 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08743 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08744 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08745 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08745 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08755 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08757 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08759 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08761 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08778 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08786 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08786 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08788 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08846 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08852 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08852 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08852 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08855 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08858 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0887 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0887 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0888 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0889 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08932 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08932 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08948 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08993 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09061 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09062 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0914 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09148 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09166 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09341 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09346 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0958 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0958 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10609 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10609 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12798 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12858 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13406 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14463 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06217 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06217 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06217 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07476 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07485 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0759 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0759 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07604 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0761 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0761 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07611 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07613 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07613 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07617 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07617 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07619 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07619 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07619 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0762 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07621 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07621 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07621 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0763 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07632 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07633 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07635 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0765 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07657 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07657 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07658 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07709 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07714 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07714 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07714 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07717 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07719 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0773 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0773 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07739 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07747 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07784 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07784 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07798 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07837 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07896 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07897 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07965 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07972 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07988 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08141 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08144 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08349 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08349 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09246 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09246 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11153 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11205 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11683 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13954 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0507 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-188 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07731 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08085 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08534 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08585 | 101.14 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08956 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09796 | 108.05 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09796 | 108.5 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09796 | 108.5 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09825 | 109.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09825 | 109.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.0987 | 109.93 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13008 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13425 | 110.53 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14407 | 111.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14407 | 112.37 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14407 | 112.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14435 | 113.15 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14435 | 113.15 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14481 | 113.77 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08956 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.13196 | 143.58 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17132 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17218 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17221 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17228 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17233 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17233 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17234 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17234 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17235 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17236 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17236 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17236 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17236 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1724 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17242 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17243 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17244 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17253 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17256 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17256 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17257 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17283 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17287 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17289 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1729 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1729 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17298 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17299 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17299 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17299 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17313 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17328 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17328 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17344 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17367 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1737 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17371 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17431 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17435 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17444 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17501 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17502 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17535 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17614 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17614 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17905 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17963 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18029 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18029 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18511 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18585 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1869 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1869 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1869 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1869 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1869 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1869 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19423 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22479 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22479 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22479 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22492 | 172.27 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22492 | 172.27 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2252 | 172.75 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.22112 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22397 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.22112 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22397 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0944 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16798 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16969 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16976 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16976 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16977 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16983 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16983 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16986 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16986 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16986 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16988 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16988 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16988 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16997 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16999 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17004 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1701 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1702 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17026 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17026 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17029 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17078 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17087 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1709 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1709 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1709 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17102 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17108 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17108 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17108 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17182 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17183 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17215 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1722 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17221 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17224 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17257 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17257 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17356 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17364 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17382 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17499 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1755 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17612 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1767 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1767 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18337 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18337 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19238 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19655 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28114 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08227 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14638 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14775 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14775 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14787 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14794 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14794 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14795 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14797 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14797 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.148 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.148 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14802 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14802 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14803 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14805 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14805 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14805 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14805 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14812 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14814 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14818 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14823 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14833 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14838 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14838 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1484 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14883 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1489 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14893 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14894 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14894 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14904 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14909 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14909 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14909 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14974 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14974 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15002 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15007 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15008 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1501 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15039 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15039 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15125 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15132 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15148 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15249 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15294 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15348 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15398 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15398 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1598 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1598 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16765 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17129 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18124 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18124 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18124 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27125 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1092 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21816 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21828 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21832 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21834 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21834 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2185 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2185 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21855 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21858 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21859 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21859 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21956 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21972 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22007 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22007 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22032 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22033 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22034 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22209 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22221 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22247 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2225 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22253 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22261 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22404 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2248 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22487 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22487 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22678 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23706 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24605 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24605 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24605 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26463 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36784 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40849 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40972 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41332 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41332 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41332 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41332 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2175 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2428 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36752 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40809 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4093 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41289 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41289 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41289 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41289 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0944 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16798 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16969 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16976 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16976 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16977 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16983 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16983 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16986 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16986 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16986 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16988 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16988 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16988 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16997 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16999 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17004 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1701 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1702 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17026 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17026 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17029 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17078 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17087 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1709 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1709 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1709 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17108 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17108 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17108 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17137 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17182 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17183 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17215 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1722 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17221 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17224 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17257 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17257 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17356 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17364 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17382 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17499 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1755 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17612 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1767 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1767 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18337 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18337 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19238 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19655 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19748 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28114 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08227 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14638 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14775 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14775 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14787 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14794 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14794 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14795 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14797 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14797 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.148 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.148 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14802 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14802 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14803 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14805 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14805 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14805 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14805 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14812 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14814 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14818 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14823 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14833 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14838 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14838 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1484 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14883 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1489 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14893 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14894 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14894 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14909 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14909 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14909 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14935 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14974 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14974 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15002 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15007 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15008 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1501 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15039 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15039 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15125 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15132 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15148 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15249 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15294 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15348 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15398 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15398 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1598 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1598 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16765 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17129 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17209 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18124 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18124 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18124 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27125 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0779 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08121 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05924 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07679 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05924 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05987 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06104 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0613 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06404 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06421 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06424 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06431 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06436 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06436 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06437 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06437 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06437 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06438 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06438 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06438 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06438 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06443 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06445 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06445 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06447 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06456 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0646 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0646 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0646 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06465 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06487 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06489 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06493 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06494 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06494 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06495 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06502 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06502 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06503 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06503 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06505 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06511 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06522 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0655 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06573 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06605 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06605 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06641 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06645 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06655 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06728 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0675 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0687 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0687 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07434 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07434 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07635 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09069 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09069 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09069 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09069 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09069 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09069 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.102 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07554 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07554 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07554 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09045 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09166 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09213 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09242 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09242 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09257 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09264 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09267 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09267 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09268 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09268 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09272 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09272 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09275 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09275 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09275 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09276 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09277 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09277 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09286 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09288 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09292 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09295 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09309 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09317 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09317 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09319 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09373 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09381 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09381 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09382 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09385 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.094 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.094 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09405 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09408 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09423 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09466 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09466 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09476 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0952 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09564 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09565 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0966 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09668 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09686 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09834 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09861 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10055 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10055 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10969 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10969 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13149 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14201 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15344 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06583 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06583 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06583 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07883 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07988 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08029 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08054 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08054 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08067 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08073 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08074 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08076 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08076 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0808 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0808 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08082 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08082 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08083 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08084 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08084 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08084 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08084 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08093 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08094 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08098 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.081 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08113 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08119 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08119 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08121 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08168 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08176 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08176 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08176 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08178 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08191 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08191 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08196 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08199 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08212 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08249 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08249 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08258 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08297 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08335 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08336 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08418 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08425 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08441 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0857 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08593 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08763 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08763 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12375 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14804 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.07506 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15415 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16947 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16947 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16947 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18175 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18175 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1826 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18411 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18423 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18423 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18423 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18428 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18447 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18449 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18449 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18456 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18466 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18498 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18498 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18566 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18629 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18701 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18702 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18818 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18829 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18855 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18858 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18862 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19057 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19098 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19105 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19105 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19405 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20079 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20807 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26487 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26576 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34549 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34685 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34821 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34821 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34821 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34821 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.1909 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24302 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26553 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34514 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34651 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34785 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34785 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34785 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34785 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07554 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07554 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07554 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09045 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09166 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09213 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09242 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09242 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09257 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09264 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09267 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09267 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09268 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09272 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09272 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09275 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09275 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09275 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09276 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09277 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09277 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09286 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09288 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09292 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09295 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09309 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09317 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09317 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09319 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09373 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09381 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09381 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09382 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09385 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09386 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.094 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.094 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09405 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09423 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09466 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09466 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09476 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0952 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09564 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09565 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0966 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09668 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09686 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09834 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09861 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10055 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10055 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10969 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10969 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13149 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14201 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14267 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15344 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06583 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06583 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06583 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07883 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07988 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08029 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08054 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08054 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08067 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08073 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08074 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08076 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08076 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0808 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0808 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08082 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08082 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08083 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08084 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08084 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08084 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08084 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08093 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08094 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08098 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.081 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08113 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08119 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08119 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08121 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08168 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08176 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08176 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08176 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08178 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0818 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08191 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08191 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08196 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08212 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08249 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08249 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08258 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08297 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08335 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08336 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08418 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08425 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08441 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0857 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08593 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08763 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08763 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12375 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12433 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14804 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08081 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08527 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.0607 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.05015 | 110.53 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07516 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.0607 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0514 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0514 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0514 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05178 | 172.27 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05178 | 172.27 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05244 | 172.75 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.057 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05702 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0571 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05761 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05782 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05785 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05792 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05797 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05797 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05798 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05798 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05798 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05799 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05799 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.058 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.058 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05804 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05805 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05805 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05808 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05816 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0582 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0582 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05821 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05846 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05848 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0585 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05852 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05853 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05853 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05861 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05862 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05862 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05863 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05863 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05864 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05877 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05908 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05931 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05941 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05941 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05993 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05997 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06007 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06057 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06097 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06648 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06648 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07484 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08944 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09022 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09022 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09022 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09022 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09022 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09022 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09861 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10305 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10449 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10451 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10451 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10466 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10474 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10474 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10477 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10477 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10477 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10477 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10481 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10481 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10484 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10486 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10486 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10486 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10495 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10496 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10501 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10502 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10518 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10524 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10524 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10527 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10575 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10583 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10586 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10588 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10588 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10602 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10605 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10605 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10605 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1063 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10672 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10672 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10681 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10723 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1073 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10731 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10851 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1086 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10878 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10982 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11045 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1118 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1118 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11928 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11928 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13723 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16523 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17347 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08594 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08715 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08715 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08715 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0898 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09106 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09108 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09108 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09121 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09127 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09128 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0913 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0913 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09134 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09134 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09136 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09136 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09136 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09138 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09138 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09138 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09138 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09146 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09147 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09151 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09153 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09166 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09171 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09171 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09174 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09216 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09223 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09226 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09227 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09227 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09239 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09241 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09242 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09242 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09263 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09301 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09301 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09308 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09344 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09351 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09352 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09456 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09464 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09479 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0957 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09625 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09743 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09743 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10395 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10395 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11959 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14399 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16736 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10757 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21147 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21147 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21147 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21489 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21489 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21652 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21664 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21668 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21671 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21671 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21694 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21695 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21695 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21696 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21696 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21746 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21746 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21811 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21815 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2187 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21888 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2189 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22043 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22055 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22081 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22084 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22088 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22222 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22313 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2232 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2232 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22534 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23356 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23684 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28391 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30922 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40565 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40667 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41022 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41022 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41022 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41022 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2173 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26049 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30895 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40525 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40625 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4098 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4098 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4098 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4098 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09861 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10305 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10449 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10451 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10451 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10466 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10474 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10474 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10477 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10477 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10477 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10481 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10481 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10484 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10486 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10486 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10486 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10495 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10496 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10501 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10502 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10518 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10524 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10524 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10527 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10575 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10583 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10586 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10588 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10588 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10598 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10605 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10605 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10605 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1063 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10672 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10672 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10681 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10723 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1073 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10731 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10851 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1086 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10878 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10982 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11045 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1118 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1118 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11928 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11928 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13723 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16523 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16601 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17347 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08594 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08715 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08715 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08715 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0898 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09106 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09108 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09108 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09121 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09127 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09128 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0913 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0913 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09134 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09134 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09136 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09136 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09136 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09138 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09138 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09138 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09138 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09146 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09147 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09151 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09153 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09166 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09171 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09171 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09174 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09216 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09223 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09226 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09227 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09227 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09235 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09241 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09242 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09242 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09263 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09301 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09301 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09308 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09344 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09351 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09352 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09456 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09464 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09479 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0957 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09625 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09743 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09743 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10395 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10395 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11959 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14399 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14467 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16736 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07194 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07309 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05679 | 115.41 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05679 | 115.42 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05679 | 115.42 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05679 | 115.46 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05679 | 115.46 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05679 | 114.08 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05679 | 114.1 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05679 | 114.1 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05679 | 114.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05679 | 114.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0961 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09938 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09938 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09953 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0996 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09961 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09961 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09963 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09963 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09963 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09963 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09968 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09968 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09971 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09972 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09972 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09972 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09974 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09974 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09986 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09987 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09989 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10007 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10017 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10017 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10018 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10042 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10069 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10086 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10086 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10093 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10093 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10101 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10103 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10103 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10103 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10104 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10104 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10104 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10119 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10134 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10177 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10225 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1025 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10251 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1041 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10417 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10436 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10632 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10754 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10823 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10839 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10839 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10865 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10865 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11089 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11383 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11482 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11482 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16496 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08374 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0866 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0866 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08674 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0868 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0868 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08683 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08683 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08687 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08687 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0869 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0869 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0869 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0869 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0869 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08692 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08692 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08702 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08703 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08705 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0872 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08729 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08729 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0873 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08751 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08775 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0879 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0879 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08795 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08796 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08803 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08804 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08804 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08804 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08806 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08806 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08806 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08819 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08832 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08869 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08911 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08933 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08933 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09072 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09078 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09094 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09265 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09372 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09432 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09446 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09446 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09469 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09469 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09664 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0992 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10006 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10006 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15916 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11694 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11998 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12232 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1244 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12549 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12549 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12549 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12616 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12616 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12625 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12637 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12642 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12642 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12642 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12669 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12683 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12754 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12822 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12866 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12868 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13074 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13084 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13111 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13113 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13118 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13384 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13392 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13392 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13409 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13409 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13465 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13516 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13516 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13551 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13712 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14713 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21303 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23593 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23723 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23723 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23723 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23723 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24089 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.1073 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.13499 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21284 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23569 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23699 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23699 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23699 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23699 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24065 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0961 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09938 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09938 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09953 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0996 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09961 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09961 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09963 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09963 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09963 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09968 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09968 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09971 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09972 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09972 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09972 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09974 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09974 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09986 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09987 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09989 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10007 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10017 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10017 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10018 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10042 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10069 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10086 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10086 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10093 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10093 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10101 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10103 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10103 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10103 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10104 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10104 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10104 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10134 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10177 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10225 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1025 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10251 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10328 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1041 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10417 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10436 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10632 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10754 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10823 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10839 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10839 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10865 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10865 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11089 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11383 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11437 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11482 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11482 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16496 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08374 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0866 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0866 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08674 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0868 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0868 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08683 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08683 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08687 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08687 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0869 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0869 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0869 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0869 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0869 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08692 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08692 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08702 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08703 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08705 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0872 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08729 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08729 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0873 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08751 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08775 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0879 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0879 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08795 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08796 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08803 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08804 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08804 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08804 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08806 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08806 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08806 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08832 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08869 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08911 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08933 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08933 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09072 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09078 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09094 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09265 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09372 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09432 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09446 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09446 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09469 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09469 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09664 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0992 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09967 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10006 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10006 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15916 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07286 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07438 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05566 | 115.41 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05566 | 115.42 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05566 | 115.42 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05566 | 115.46 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05566 | 115.46 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05566 | 114.08 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05566 | 114.1 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05566 | 114.1 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05566 | 114.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05566 | 114.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05019 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05019 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1074 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10944 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10944 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1096 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10967 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10967 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1097 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1097 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1097 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1097 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10975 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10975 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10978 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10978 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10978 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10979 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1098 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1098 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10992 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10993 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10995 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11013 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11023 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11023 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11024 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11041 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11067 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1109 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11091 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11091 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11096 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11105 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11108 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1111 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1111 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11123 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11138 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11183 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1123 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11251 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11252 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11258 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11258 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11258 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11409 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11416 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11435 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11628 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11733 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11781 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11824 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11824 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11826 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11826 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12045 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12377 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12462 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12462 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18163 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0936 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09538 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09538 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09551 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09557 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09557 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0956 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0956 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09564 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09564 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09567 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09567 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09567 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09568 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09568 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09569 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09569 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09579 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0958 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09582 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09598 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09606 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09606 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09607 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09622 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09644 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09665 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09666 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09666 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0967 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09677 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0968 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09682 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09682 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09693 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09706 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09746 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09786 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09805 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09806 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09811 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09811 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09811 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09943 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09949 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09965 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10134 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10225 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10267 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10304 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10304 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10306 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10306 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10497 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10786 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1086 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1086 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17524 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12924 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13009 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1324 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13407 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13581 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13581 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13588 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13599 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13604 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13607 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13607 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13629 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13629 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13629 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13631 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13646 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13719 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13786 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13825 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13826 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14031 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14041 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14067 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14069 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14075 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14332 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14332 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14336 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14344 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14344 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14374 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14425 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14425 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14479 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14652 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15641 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23162 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25413 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25567 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25567 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25567 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25567 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25844 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.11857 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.1435 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23142 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25387 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2554 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2554 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2554 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2554 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25819 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1074 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10944 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10944 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1096 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10967 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10967 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1097 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1097 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1097 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10975 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10975 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10978 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10978 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10978 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10979 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1098 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1098 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10992 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10993 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10995 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11013 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11023 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11023 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11024 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11041 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11067 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1109 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11091 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11091 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11096 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11105 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11108 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1111 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1111 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11138 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11183 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1123 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11251 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11252 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11258 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11258 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11258 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11312 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11409 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11416 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11435 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11628 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11733 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11781 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11824 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11824 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11826 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11826 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12045 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12377 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12435 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12462 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12462 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18163 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0936 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09538 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09538 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09551 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09557 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09557 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0956 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0956 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09564 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09564 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09567 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09567 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09567 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09568 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09568 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09569 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09569 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09579 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0958 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09582 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09598 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09606 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09606 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09607 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09622 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09644 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09665 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09666 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09666 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0967 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09677 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0968 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09682 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09682 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09706 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09746 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09786 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09805 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09806 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09811 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09811 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09811 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09858 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09943 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09949 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09965 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10134 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10225 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10267 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10304 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10304 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10306 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10306 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10497 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10786 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10836 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1086 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1086 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17524 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0761 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-228 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08529 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07883 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.0825 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05883 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07512 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05883 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05381 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05749 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05769 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05953 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05991 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05994 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06001 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06006 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06006 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06007 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06007 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06007 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06008 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06008 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06009 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06009 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06013 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06014 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06015 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06017 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06019 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06026 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0603 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0603 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0603 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06056 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06058 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06062 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06063 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06063 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06064 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06071 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06071 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06073 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06073 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06074 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06079 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06086 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06119 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06142 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06167 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06168 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06208 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06212 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06222 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06288 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06316 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06425 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06425 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06959 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06959 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07275 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08983 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08983 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08983 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08983 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08983 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08983 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09638 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07767 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07767 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07767 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08781 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08999 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09005 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09065 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09065 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0908 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09087 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09088 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09088 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09091 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09091 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09095 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09095 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09097 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09097 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09098 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09099 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.091 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.091 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09109 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09111 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09115 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09117 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09132 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09139 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09139 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09141 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09194 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09202 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09203 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09203 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09205 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09222 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09222 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09225 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09226 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09242 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09285 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09285 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09298 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09341 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09375 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09477 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09485 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09504 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09637 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09676 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09852 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09852 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10716 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10716 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12836 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14675 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15051 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06769 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06769 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06769 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07652 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07842 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07848 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.079 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.079 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07913 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07919 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0792 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07922 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07922 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07926 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07926 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07928 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07928 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07928 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0793 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0793 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0793 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0793 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07938 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0794 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07944 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07945 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07958 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07964 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07964 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07966 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08012 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08019 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0802 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0802 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08022 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08036 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08036 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08039 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0804 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08054 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08092 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08092 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08103 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08141 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08169 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0817 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08259 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08266 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08282 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08398 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08432 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08586 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08586 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09339 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09339 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11186 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12789 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14521 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.08538 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18278 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18278 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18278 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1922 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1922 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19292 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19439 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19451 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19454 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19454 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19456 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19474 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19479 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19479 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19484 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19491 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19596 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19658 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19713 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19714 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19841 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19853 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19878 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19881 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19885 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2006 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20118 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20125 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20125 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20398 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21451 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21725 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27231 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27464 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28633 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3649 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36551 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36789 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36789 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36789 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36789 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.19932 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24984 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2744 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36453 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36515 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36751 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36751 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36751 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36751 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07767 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07767 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07767 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08781 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08999 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09005 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09065 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09065 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0908 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09087 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09088 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09088 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09091 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09095 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09095 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09097 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09097 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09098 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09099 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.091 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.091 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09109 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09111 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09115 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09117 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09132 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09139 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09139 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09141 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09194 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09202 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09203 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09203 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09205 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09209 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09222 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09222 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09225 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09242 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09285 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09285 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09298 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09341 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09375 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09477 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09485 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09504 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09637 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09676 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09852 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09852 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10716 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10716 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12836 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14675 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14744 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15051 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06769 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06769 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06769 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07652 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07842 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07848 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.079 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.079 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07913 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07919 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0792 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07922 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07922 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07926 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07926 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07928 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07928 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07928 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0793 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0793 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0793 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0793 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07938 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0794 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07944 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07945 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07958 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07964 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07964 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07966 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08012 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08019 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0802 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0802 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08022 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08025 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08036 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08036 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08039 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08054 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08092 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08092 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08103 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08141 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08169 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0817 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08259 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08266 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08282 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08398 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08432 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08586 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08586 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09339 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09339 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11186 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12789 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12849 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14521 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09707 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-237 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.10786 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Non-Converged | DISIS-2023-001 | 00ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 00ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 00ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 04NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 05NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 04ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 04ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 04ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 04ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-001 |  | Non-Converged |  |  | 0.04877 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-001 |  | Non-Converged |  |  | 0.04891 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.04936 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-005 |  | Non-Converged |  |  | 0.06498 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-005 |  | Non-Converged |  |  | 0.06438 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.06393 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-060 |  | Non-Converged |  |  | 0.06498 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-060 |  | Non-Converged |  |  | 0.06438 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.06393 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-142 |  | Non-Converged |  |  | 0.06498 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-142 |  | Non-Converged |  |  | 0.06438 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.06393 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-143 |  | Non-Converged |  |  | 0.06498 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-143 |  | Non-Converged |  |  | 0.06438 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.06393 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-158 |  | Non-Converged |  |  | 0.75464 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-158 |  | Non-Converged |  |  | 0.75508 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.75553 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-159 |  | Non-Converged |  |  | 0.75464 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-159 |  | Non-Converged |  |  | 0.75508 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.75553 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-176 |  | Non-Converged |  |  | 0.06498 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-176 |  | Non-Converged |  |  | 0.06438 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-176 |  | Non-Converged |  |  | 0.06393 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-178 |  | Non-Converged |  |  | 0.06738 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-178 |  | Non-Converged |  |  | 0.06686 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.06642 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-195 |  | Non-Converged |  |  | 0.07453 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-195 |  | Non-Converged |  |  | 0.07402 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.07358 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-203 |  | Non-Converged |  |  | 0.07064 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-203 |  | Non-Converged |  |  | 0.0708 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.07125 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-236 |  | Non-Converged |  |  | 0.03516 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-236 |  | Non-Converged |  |  | 0.03528 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.03573 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 | 00NR | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 00NR | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 00NR | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-227 | FROM->TO | 508284 ADORA 2 69.0 508285 ADORA T2 69.0 1 | 76 | 76 | 0.09953 | 105.51 | P12:138:AEPW:CAMPCOR4:PITTSB_4::: | TDF Impact | ADORA2 to ADORAT2 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-227 | FROM->TO | 508284 ADORA 2 69.0 508285 ADORA T2 69.0 1 | 76 | 76 | 0.09955 | 107.46 | P12:138:AEPW:CAMPCOR4:PITTSB_4::: | TDF Impact | ADORA2 to ADORAT2 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 463 | 481 | 0.04278 | 107.96 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 463 | 481 | 0.0555 | 107.96 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 463 | 481 | 0.03353 | 107.96 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 463 | 481 | 0.76196 | 107.96 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-028 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 463 | 481 | 0.04165 | 108.68 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-049 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 463 | 481 | 0.05447 | 108.68 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 463 | 481 | 0.03379 | 108.68 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 463 | 481 | 0.76316 | 108.68 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-194 | FROM->TO | 547525 JOP 59 2 69.0 547541 RIV167 2 69.0 1 | 72 | 72 | 0.07333 | 100.86 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the existing JOP 59 2 to RIV167 2 69 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-028 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 548 | 558 | 0.04491 | 106.75 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-049 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 548 | 558 | 0.05794 | 106.75 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-050 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 548 | 558 | 0.03442 | 106.75 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 548 | 558 | 0.76078 | 106.75 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Rebuild the existing RIV4525 to STL439_5 161 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547525 JOP 59 2 69.0 547541 RIV167 2 69.0 1 | 72 | 72 | 0.07285 | 113.03 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the existing JOP 59 2 to RIV167 2 69 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.12427 | 100.31 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.13845 | 107.6 | P21:161:GRDA:12SUB-KANSATP5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.13845 | 108.67 | P12:161:GRDA:KERR GR5-412SUB 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.13884 | 107.44 | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.21343 | 122.61 | P12:161:GRDA:KERR GR5-MAID-2 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.12411 | 100.19 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.13826 | 107.46 | P21:161:GRDA:12SUB-KANSATP5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.13826 | 108.53 | P12:161:GRDA:KERR GR5-412SUB 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.13865 | 107.31 | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-027 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.21336 | 122.58 | P12:161:GRDA:KERR GR5-MAID 5-1:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.06697 | 107.6 | P21:161:GRDA:12SUB-KANSATP5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.06697 | 108.67 | P12:161:GRDA:KERR GR5-412SUB 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.0674 | 107.44 | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.08969 | 122.61 | P12:161:GRDA:KERR GR5-MAID-2 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.22764 | 100.31 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.06688 | 107.46 | P21:161:GRDA:12SUB-KANSATP5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.06688 | 108.53 | P12:161:GRDA:KERR GR5-412SUB 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.0673 | 107.31 | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.08966 | 122.58 | P12:161:GRDA:KERR GR5-MAID 5-1:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-028 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.22733 | 100.19 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.09824 | 107.6 | P21:161:GRDA:12SUB-KANSATP5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.09824 | 108.67 | P12:161:GRDA:KERR GR5-412SUB 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.09875 | 107.44 | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.14553 | 122.61 | P12:161:GRDA:KERR GR5-MAID-2 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.22764 | 100.31 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.09811 | 107.46 | P21:161:GRDA:12SUB-KANSATP5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.09811 | 108.53 | P12:161:GRDA:KERR GR5-412SUB 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.09862 | 107.31 | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.14548 | 122.58 | P12:161:GRDA:KERR GR5-MAID 5-1:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-049 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.22733 | 100.19 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-055 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.40155 | 100.31 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-055 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.43652 | 107.6 | P21:161:GRDA:12SUB-KANSATP5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-055 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.43652 | 108.67 | P12:161:GRDA:KERR GR5-412SUB 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-055 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.43677 | 107.44 | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-055 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.69424 | 122.61 | P12:161:GRDA:KERR GR5-MAID-2 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-055 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.401 | 100.19 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-055 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.43593 | 107.46 | P21:161:GRDA:12SUB-KANSATP5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-055 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.43593 | 108.53 | P12:161:GRDA:KERR GR5-412SUB 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-055 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.43618 | 107.31 | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-055 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.694 | 122.58 | P12:161:GRDA:KERR GR5-MAID 5-1:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-057 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.03231 | 122.61 | P12:161:GRDA:KERR GR5-MAID-2 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-057 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.0323 | 122.58 | P12:161:GRDA:KERR GR5-MAID 5-1:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-061 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.03235 | 100.31 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-061 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.03449 | 122.61 | P12:161:GRDA:KERR GR5-MAID-2 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-061 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.0323 | 100.19 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-061 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.03448 | 122.58 | P12:161:GRDA:KERR GR5-MAID 5-1:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.03613 | 100.31 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 1 | 198 | 198 | 0.06301 | 122.61 | P12:161:GRDA:KERR GR5-MAID-2 5:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 1 Rebuild #2
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.03608 | 100.19 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-213 | FROM->TO | 512635 KERR GR5 161 512648 MAID 5 161 2 | 198 | 198 | 0.06299 | 122.58 | P12:161:GRDA:KERR GR5-MAID 5-1:::HV: | TDF Impact | Kerr - Maid 161 kV Ckt 2 Rebuild
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-032 | FROM->TO | 541264 LEX69 2 69.0 541232 LEX161 5 161 1 | 50 | 55 | 0.11775 | 100.05 | 541229 ODESSA 5 161 772620 G23-032-TAP 161 1 | TDF Impact | Upgrade the existing LEX161 5 161/69 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-032 | FROM->TO | 541264 LEX69 2 69.0 541232 LEX161 5 161 1 | 50 | 55 | 0.11742 | 105.29 | 541229 ODESSA 5 161 772620 G23-032-TAP 161 1 | TDF Impact | Upgrade the existing LEX161 5 161/69 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-216 | FROM->TO | 640227 HOSKINS4 230 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 105.86 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-216 | FROM->TO | 640227 HOSKINS4 230 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 112.21 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-216 | FROM->TO | 640228 HOSKINS7 115 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 104.66 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-216 | FROM->TO | 640228 HOSKINS7 115 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 111.12 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-217 | FROM->TO | 640227 HOSKINS4 230 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 105.86 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-217 | FROM->TO | 640227 HOSKINS4 230 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 112.21 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-217 | FROM->TO | 640228 HOSKINS7 115 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 104.66 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-217 | FROM->TO | 640228 HOSKINS7 115 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 111.12 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-218 | FROM->TO | 640227 HOSKINS4 230 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 105.86 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-218 | FROM->TO | 640227 HOSKINS4 230 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 112.21 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-218 | FROM->TO | 640228 HOSKINS7 115 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 104.66 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-218 | FROM->TO | 640228 HOSKINS7 115 996836 HOSKINS T1 115 1 | 187 | 187 | 0.04326 | 111.12 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-216 | FROM->TO | 640227 HOSKINS4 230 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 106.6 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-216 | FROM->TO | 640227 HOSKINS4 230 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 113.5 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-216 | FROM->TO | 640228 HOSKINS7 115 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 106.05 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-216 | FROM->TO | 640228 HOSKINS7 115 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 112.83 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-217 | FROM->TO | 640227 HOSKINS4 230 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 106.6 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-217 | FROM->TO | 640227 HOSKINS4 230 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 113.5 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-217 | FROM->TO | 640228 HOSKINS7 115 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 106.05 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-217 | FROM->TO | 640228 HOSKINS7 115 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 112.83 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-218 | FROM->TO | 640227 HOSKINS4 230 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 106.6 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-218 | FROM->TO | 640227 HOSKINS4 230 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 113.5 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-218 | FROM->TO | 640228 HOSKINS7 115 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 106.05 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-218 | FROM->TO | 640228 HOSKINS7 115 996833 HOSKINS T1 115 1 | 187 | 187 | 0.04332 | 112.83 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-216 | FROM->TO | 640227 HOSKINS4 230 996833 HOSKINS T1 115 1 | 187 | 187 | 0.0434 | 103.78 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-216 | FROM->TO | 640228 HOSKINS7 115 996833 HOSKINS T1 115 1 | 187 | 187 | 0.0434 | 102.12 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-217 | FROM->TO | 640227 HOSKINS4 230 996833 HOSKINS T1 115 1 | 187 | 187 | 0.0434 | 103.78 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-217 | FROM->TO | 640228 HOSKINS7 115 996833 HOSKINS T1 115 1 | 187 | 187 | 0.0434 | 102.12 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-218 | FROM->TO | 640227 HOSKINS4 230 996833 HOSKINS T1 115 1 | 187 | 187 | 0.0434 | 103.78 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 27WP | GEN-2023-218 | FROM->TO | 640228 HOSKINS7 115 996833 HOSKINS T1 115 1 | 187 | 187 | 0.0434 | 102.12 | P13:115-345:NPPD:NUCOR-2 | TDF Impact | Upgrade existing HOSKINS T1 230/115 kV Transformer
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.05434 | 102.67 | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.05434 | 107.1 | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-038 | FROM->TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.05441 | 104.18 | P12:138:OKGE:BKRBKR6:::: | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.0495 | 102.67 | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.0495 | 107.1 | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-069 | FROM->TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.04957 | 104.18 | P12:138:OKGE:BKRBKR6:::: | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.06599 | 102.67 | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.06599 | 107.1 | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-092 | FROM->TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.06608 | 104.18 | P12:138:OKGE:BKRBKR6:::: | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 24SP | GEN-2023-134 | FROM->TO | 515073 ERLSBOR2 69.0 515074 FRSTHIL2 69.0 1 | 39 | 48 | 0.04901 | 111.55 | P12:138:OKGE:BKRBKR224:::: | TDF Impact | Rebuild the existing ERLSBOR2 to FRSTHIL2 69 kV line
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.05222 | 106.22 | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.05229 | 103.17 | P12:138:OKGE:BKRBKR6:::: | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.05222 | 110.81 | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-038 | FROM->TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.05229 | 107.76 | P12:138:OKGE:BKRBKR6:::: | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.04774 | 106.22 | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.04781 | 103.17 | P12:138:OKGE:BKRBKR6:::: | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.04774 | 110.81 | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2023-001 | 00NR | 1 | 27SP | GEN-2023-069 | FROM->TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.04781 | 107.76 | P12:138:OKGE:BKRBKR6:::: | TDF Impact | Brown Substation Expansion